## 1- Syst_Loc1 Missing
CENTRE | AREA_NAME | UNIT_NUMBER | LOOP_NAME | TAG_NUMBER | PID | SYSTEM1 | IO_TYPE1 | SYST_LOC1 | MISSING_SYST_LOC1
KA | HL | 64 INERT GAS & NITROGEN | 64X04301 | 64HY 04301A | 076328C-KA-43-P-XB-4330 | PCS | DO |  | Syst_Loc1 is not filled
KA | HL | 64 INERT GAS & NITROGEN | 64X04301 | 64XY 04301B | 076328C-KA-43-P-XB-4330 | PSD | DO |  | Syst_Loc1 is not filled
KA | HL | 64 INERT GAS & NITROGEN | 64X04301 | 64ZLC 04301 | 076328C-KA-43-P-XB-4330 | PCS | SOFT |  | Syst_Loc1 is not filled
| HL | 64 INERT GAS & NITROGEN | 64X04301 | 64ZLO 04301 | 076328C-KA-43-P-XB-4330 | PCS | SOFT |  | Syst_Loc1 is not filled
KA | HL | 64 INERT GAS & NITROGEN | 64X04301 | 64ZSC 04301 | 076328C-KA-43-P-XB-4330 | PCS | DI |  | Syst_Loc1 is not filled
KA | HL | 64 INERT GAS & NITROGEN | 64X04301 | 64ZSO 04301 | 076328C-KA-43-P-XB-4330 | PCS | DI |  | Syst_Loc1 is not filled
KA | HL | 64 INERT GAS & NITROGEN | 64X04301 | 64ZXA 04301 | 076328C-KA-43-P-XB-4330 | PCS | SOFT |  | Syst_Loc1 is not filled
| HL | 65 HYDRAULIC DISTRIBUTION | 65H20003 | 65HY 20003 | 076328C-SC-50-L-XB-5056 | PCS | DO |  | Syst_Loc1 is not filled
| HL | 65 HYDRAULIC DISTRIBUTION | 65H20003 | 65ZLC 20003 | 076328C-SC-50-L-XB-5056 | PCS | SOFT |  | Syst_Loc1 is not filled
| HL | 65 HYDRAULIC DISTRIBUTION | 65H20003 | 65ZLO 20003 | 076328C-SC-50-L-XB-5056 | PCS | SOFT |  | Syst_Loc1 is not filled
SC | HL | 65 HYDRAULIC DISTRIBUTION | 65H20003 | 65ZSC 20003 | 076328C-SC-50-L-XB-5056 | PCS | DI |  | Syst_Loc1 is not filled
| HL | 65 HYDRAULIC DISTRIBUTION | 65H20003 | 65ZSO 20003 | 076328C-SC-50-L-XB-5056 | PCS | DI |  | Syst_Loc1 is not filled
| HL | 65 HYDRAULIC DISTRIBUTION | 65H20003 | 65ZXA 20003 | 076328C-SC-50-L-XB-5056 | PCS | SOFT |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 13E00101 | 13EY 00101 | 076328C-KA-13-P-XB-1301 | ESD | AO |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 13E00201 | 13EY 00201 | 076328C-KA-13-P-XB-1302 | ESD | AO |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+102 | 13XY 00101 | 076328C-KA-13-P-XB-1301 | PSD | DO |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+102 | 13XY 00101B | 076328C-KA-13-P-XB-1301 | ESD | DO |  | Syst_Loc1 is not filled
| TS | 13 RISER AND WELL SYSTEM | 1.3e+202 | 13XY 00201 |  | PSD | DO |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+202 | 13XY 00201B | 076328C-KA-13-P-XB-1302 | ESD | DO |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+102 | 13ZLC 00101 | 076328C-KA-13-P-XB-1301 | PCS | SOFT |  | Syst_Loc1 is not filled
| TS | 13 RISER AND WELL SYSTEM | 1.3e+202 | 13ZLC 00201 |  | PCS | SOFT |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+102 | 13ZLO 00101 | 076328C-KA-13-P-XB-1301 | PCS | SOFT |  | Syst_Loc1 is not filled
| TS | 13 RISER AND WELL SYSTEM | 1.3e+202 | 13ZLO 00201 |  | PCS | SOFT |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+102 | 13ZSC 00101 | 076328C-KA-13-P-XB-1301 | PCS | DI |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+102 | 13ZSO 00101 | 076328C-KA-13-P-XB-1301 | PCS | DI |  | Syst_Loc1 is not filled
KA | TS | 13 RISER AND WELL SYSTEM | 1.3e+102 | 13ZXA 00101 | 076328C-KA-13-P-XB-1301 | PCS | SOFT |  | Syst_Loc1 is not filled
| TS | 38 MEG REGENERATION AND INJECTION | 38P1201 | 38PDAH 1201 |  | PCS | SOFT |  | Syst_Loc1 is not filled
| TS | 38 MEG REGENERATION AND INJECTION | 38P1201 | 38PDAL 01201 |  | PCS | SOFT |  | Syst_Loc1 is not filled
| TS | 38 MEG REGENERATION AND INJECTION | 38P1201 | 38PDI 1201 |  | PCS | SOFT |  | Syst_Loc1 is not filled
| TS | 38 MEG REGENERATION AND INJECTION | 38P1201 | 38PDIT 01201 |  | PCS | AI |  | Syst_Loc1 is not filled
KA | TS | 38 MEG REGENERATION AND INJECTION | 38T00600A | 38TAL 00600A | 076328C-KA-38-P-XB-3806 | PCS | SOFT |  | Syst_Loc1 is not filled
KA | TS | 38 MEG REGENERATION AND INJECTION | 38T00600A | 38TI 00600A | 076328C-KA-38-P-XB-3806 | PCS | SOFT |  | Syst_Loc1 is not filled
KA | TS | 38 MEG REGENERATION AND INJECTION | 38T00600A | 38TIT 00600A | 076328C-KA-38-P-XB-3806 | PCS | HART AI |  | Syst_Loc1 is not filled
KA | TS | 38 MEG REGENERATION AND INJECTION | 38T00600B | 38TIT 00600B | 076328C-KA-38-P-XB-3806 | PCS | HART AI |  | Syst_Loc1 is not filled
Hop!

## 2- Syst_Loc1 Inconsistency
CENTRE | AREA_NAME | UNIT_NUMBER | LOOP_NAME | TAG_NUMBER | PID | SYSTEM1 | IO_TYPE1 | SYST_LOC1 | INCONS_SYST_LOC1
POC | HL | 71 FIRE WATER | 71L31001 | 71LAH 31001 | 076328C-TP002-71-Z-XB-0001 | FGS | SOFT | - | Sys_Loc1 shall be ITRQ
POC | HL | 71 FIRE WATER | 71L31001 | 71LAL 31001 | 076328C-TP002-71-Z-XB-0001 | FGS | SOFT | - | Sys_Loc1 shall be ITRQ
POC | HL | 71 FIRE WATER | 71L31002 | 71LAL 31002 | 076328C-TP002-71-Z-XB-0001 | FGS | SOFT | - | Sys_Loc1 shall be ITRQ
POC | HL | 71 FIRE WATER | 71L31001 | 71LALL 31001 | 076328C-TP002-71-Z-XB-0001 | FGS | SOFT | - | Sys_Loc1 shall be ITRQ
POC | HL | 71 FIRE WATER | 71L31001 | 71LIA 31001 | 076328C-TP002-71-Z-XB-0001 | FGS | SOFT | - | Sys_Loc1 shall be ITRQ
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-01 | 70-AB -AC02-01 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-02 | 70-AB -AC02-02 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-03 | 70-AB -AC02-03 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-04 | 70-AB -AC02-04 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-05 | 70-AB -AC02-05 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-06 | 70-AB -AC02-06 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-07 | 70-AB -AC02-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-08 | 70-AB -AC02-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-09 | 70-AB -AC02-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-10 | 70-AB -AC02-10 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-11 | 70-AB -AC02-11 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-12 | 70-AB -AC02-12 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-13 | 70-AB -AC02-13 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-14 | 70-AB -AC02-14 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC02-15 | 70-AB -AC02-15 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-01 | 70-AB -AC03-01 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-02 | 70-AB -AC03-02 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-03 | 70-AB -AC03-03 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-04 | 70-AB -AC03-04 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-05 | 70-AB -AC03-05 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-06 | 70-AB -AC03-06 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-07 | 70-AB -AC03-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-08 | 70-AB -AC03-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-09 | 70-AB -AC03-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-10 | 70-AB -AC03-10 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-11 | 70-AB -AC03-11 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-12 | 70-AB -AC03-12 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-13 | 70-AB -AC03-13 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-14 | 70-AB -AC03-14 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC03-15 | 70-AB -AC03-15 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-01 | 70-AB -AC08-01 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-02 | 70-AB -AC08-02 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-03 | 70-AB -AC08-03 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-04 | 70-AB -AC08-04 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-05 | 70-AB -AC08-05 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-06 | 70-AB -AC08-06 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-07 | 70-AB -AC08-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-08 | 70-AB -AC08-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-09 | 70-AB -AC08-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-10 | 70-AB -AC08-10 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-11 | 70-AB -AC08-11 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-12 | 70-AB -AC08-12 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-13 | 70-AB -AC08-13 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-14 | 70-AB -AC08-14 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC08-15 | 70-AB -AC08-15 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-01 | 70-AB -AC09-01 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-02 | 70-AB -AC09-02 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-03 | 70-AB -AC09-03 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-04 | 70-AB -AC09-04 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-05 | 70-AB -AC09-05 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-06 | 70-AB -AC09-06 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-07 | 70-AB -AC09-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-08 | 70-AB -AC09-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-09 | 70-AB -AC09-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-10 | 70-AB -AC09-10 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-11 | 70-AB -AC09-11 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-12 | 70-AB -AC09-12 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-13 | 70-AB -AC09-13 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-14 | 70-AB -AC09-14 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-A-AC09-15 | 70-AB -AC09-15 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-07 | 70-BF -AC02-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-08 | 70-BF -AC02-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-09 | 70-BF -AC02-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-07 | 70-BF -AC03-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-08 | 70-BF -AC03-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-09 | 70-BF -AC03-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-07 | 70-BF -AC08-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-08 | 70-BF -AC08-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-09 | 70-BF -AC08-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-07 | 70-BF -AC09-07 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-08 | 70-BF -AC09-08 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-09 | 70-BF -AC09-09 | 076328C-SI003-80-Z-XB-0013 | FGS | AI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-01 | 70-BH -AC02-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-02 | 70-BH -AC02-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-03 | 70-BH -AC02-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-04 | 70-BH -AC02-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-05 | 70-BH -AC02-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-06 | 70-BH -AC02-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-10 | 70-BH -AC02-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-02 | 70-BH -AC03-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-03 | 70-BH -AC03-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-04 | 70-BH -AC03-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-05 | 70-BH -AC03-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-06 | 70-BH -AC03-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-10 | 70-BH -AC03-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-01 | 70-BH -AC08-01 | 076328C-SI003-80-Z-XB-0013 | FGS |  | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-02 | 70-BH -AC08-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-03 | 70-BH -AC08-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-04 | 70-BH -AC08-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-05 | 70-BH -AC08-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-06 | 70-BH -AC08-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-10 | 70-BH -AC08-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-02 | 70-BH -AC09-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-03 | 70-BH -AC09-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-04 | 70-BH -AC09-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-05 | 70-BH -AC09-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-06 | 70-BH -AC09-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-10 | 70-BH -AC09-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AAC0--0 | 70-BH-AC-3-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AAC0--0 | 70-BH-AC-8-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AAC0--0 | 70-BH-AC-9-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-01 | 70-BM -AC02-01 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-02 | 70-BM -AC02-02 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC02-03 | 70-BM -AC02-03 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-01 | 70-BM -AC03-01 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-02 | 70-BM -AC03-02 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC03-03 | 70-BM -AC03-03 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-01 | 70-BM -AC08-01 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-02 | 70-BM -AC08-02 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC08-03 | 70-BM -AC08-03 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-01 | 70-BM -AC09-01 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-02 | 70-BM -AC09-02 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-B-AC09-03 | 70-BM -AC09-03 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-16 | 70-CA -AC02-16 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-16 | 70-CA -AC03-16 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-16 | 70-CA -AC08-16 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-16 | 70-CA -AC09-16 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-01 | 70-CI -AC02-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-02 | 70-CI -AC02-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-03 | 70-CI -AC02-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-04 | 70-CI -AC02-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-05 | 70-CI -AC02-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-06 | 70-CI -AC02-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-07 | 70-CI -AC02-07 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-08 | 70-CI -AC02-08 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-09 | 70-CI -AC02-09 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-10 | 70-CI -AC02-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-11 | 70-CI -AC02-11 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-12 | 70-CI -AC02-12 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-01 | 70-CI -AC03-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-02 | 70-CI -AC03-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-03 | 70-CI -AC03-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-04 | 70-CI -AC03-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-05 | 70-CI -AC03-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-06 | 70-CI -AC03-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-07 | 70-CI -AC03-07 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-08 | 70-CI -AC03-08 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-09 | 70-CI -AC03-09 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-10 | 70-CI -AC03-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-11 | 70-CI -AC03-11 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-12 | 70-CI -AC03-12 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-01 | 70-CI -AC08-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-02 | 70-CI -AC08-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-03 | 70-CI -AC08-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-04 | 70-CI -AC08-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-05 | 70-CI -AC08-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-06 | 70-CI -AC08-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-07 | 70-CI -AC08-07 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-08 | 70-CI -AC08-08 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-09 | 70-CI -AC08-09 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-10 | 70-CI -AC08-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-11 | 70-CI -AC08-11 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-12 | 70-CI -AC08-12 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-01 | 70-CI -AC09-01 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-02 | 70-CI -AC09-02 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-03 | 70-CI -AC09-03 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-04 | 70-CI -AC09-04 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-05 | 70-CI -AC09-05 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-06 | 70-CI -AC09-06 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-07 | 70-CI -AC09-07 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-08 | 70-CI -AC09-08 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-09 | 70-CI -AC09-09 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-10 | 70-CI -AC09-10 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-11 | 70-CI -AC09-11 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-12 | 70-CI -AC09-12 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC02-15 | 70-FL -AC02-15 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC03-15 | 70-FL -AC03-15 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC08-15 | 70-FL -AC08-15 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 70 FIRE AND GAS DETECTION | 70-C-AC09-15 | 70-FL -AC09-15 | 076328C-SI003-80-Z-XB-0013 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H31271 | 71HS 31271 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H32271 | 71HS 32271 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H33271 | 71HS 33271 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H34271 | 71HS 34271 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L31253 | 71LS 31253 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L31254 | 71LS 31254 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L31263 | 71LS 31263 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L31264 | 71LS 31264 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L32253 | 71LS 32253 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L32254 | 71LS 32254 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L32263 | 71LS 32263 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L32264 | 71LS 32264 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L33253 | 71LS 33253 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L33254 | 71LS 33254 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L33263 | 71LS 33263 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L33264 | 71LS 33264 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L34253 | 71LS 34253 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L34254 | 71LS 34254 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L34263 | 71LS 34263 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71L34264 | 71LS 34264 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P31244 | 71PS 31244 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P31245 | 71PS 31245 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P31251 | 71PS 31251 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P31256 | 71PS 31256 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P31257 | 71PS 31257 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P31259 | 71PS 31259 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P32244 | 71PS 32244 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P32245 | 71PS 32245 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P32251 | 71PS 32251 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P32256 | 71PS 32256 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P32257 | 71PS 32257 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P32259 | 71PS 32259 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P33244 | 71PS 33244 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P33245 | 71PS 33245 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P33251 | 71PS 33251 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P33256 | 71PS 33256 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P33257 | 71PS 33257 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P33259 | 71PS 33259 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P34244 | 71PS 34244 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P34245 | 71PS 34245 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P34251 | 71PS 34251 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P34256 | 71PS 34256 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P34257 | 71PS 34257 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71P34259 | 71PS 34259 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X31032 | 71XY 31032 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X31252 | 71XY 31252 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X31255 | 71XY 31255 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X31258 | 71XY 31258 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X32032 | 71XY 32032 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X32252 | 71XY 32252 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X32255 | 71XY 32255 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X32258 | 71XY 32258 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X33032 | 71XY 33032 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X33252 | 71XY 33252 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X33255 | 71XY 33255 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X33258 | 71XY 33258 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X34032 | 71XY 34032 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X34252 | 71XY 34252 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X34255 | 71XY 34255 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71X34258 | 71XY 34258 | 076328C-SI003-80-Z-XB-0012 | FGS | DO | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H31241 | 71ZSC 31241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H32241 | 71ZSC 32241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H33241 | 71ZSC 33241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H34241 | 71ZSC 34241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H31241 | 71ZSO 31241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H32241 | 71ZSO 32241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H33241 | 71ZSO 33241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR
POC | TS | 71 FIRE WATER | 71H34241 | 71ZSO 34241 | 076328C-SI003-80-Z-XB-0012 | FGS | DI | ITRE | Syst_Loc1 Shall be ITTR

## 3- IS_Missing
CENTRE | AREA_NAME | UNIT_NUMBER | LOOP_NAME | TAG_NUMBER | PID | SYSTEM1 | IO_TYPE1 | INTRINS | MISSING_DATA

## 4- IS_Inconsistancy
CENTRE | AREA_NAME | UNIT_NUMBER | LOOP_NAME | TAG_NUMBER | PID | IO_TYPE1 | SYSTEM1 | INTRINS | INSCONSISTENT_DATA
TOC | HL | 71 FIRE WATER | 71L31001 | 71LAH 31001 | 076328C-TP002-71-Z-XB-0001 | FGS | SOFT | - | Sys_Loc1 shall be ITRQ
TOC | HL | 71 FIRE WATER | 71L31001 | 71LAL 31001 | 076328C-TP002-71-Z-XB-0001 | FGS | SOFT | - | Sys_Loc1 shall be ITRQ