## MOTORS CHART IN AIR
LV MOTORS - CABLES LAID IN AIR
Maximum Volt Drop (%) |  |  | ΔVd | 5% |  | DERATING FACTORS | Ambient temperature factor (40°C) |  |  |  |  | 1.05
Max. Starting Volt Drop (%) |  |  | ΔVst | 15% |  |  | Layer factor |  |  |  |  | 0.8
Max Length |  |  | Lmax | 350 |  |  | Touching - LV 3-core |  |  |  |  | 0.78
[7 empty] | Trefoil untouching - LV single core |  |  |  |  | 0.9
[8 empty] | 3-CORE CABLES | [12 empty] | SINGLE-CORE CABLES
Conductor Size | [7 empty] | 3 x 4 mm² | 3 x 6 mm² | 3 x 10 mm² | 3 x 16 mm² | 3 x 25 mm² | 3 x 35 mm² | 3 x 50 mm² | 3 x 70 mm² | 3 x 95 mm² | 3 x 120 mm² | 3 x 150 mm² | 3 x 185 mm² | 3 x 240 mm² | 3 x 1 x 150 mm² | 3 x 1 x 185 mm² | 3 x 1 x 240 mm² | 3 x 1 x 300 mm² | 3 x 1 x 400 mm² | 2 x 3 x 1 x 150 mm² | 2 x 3 x 1 x 185 mm² | 2 x 3 x 1 x 240 mm² | 2 x 3 x 1 x 300 mm² | 2 x 3 x 1 x 400 mm² | 3 x 3 x 1 x 240 mm² | 3 x 3 x 1 x 300 mm² | 3 x 3 x 1 x 400 mm² | 4 x 3 x 1 x 240 mm² | 4 x 3 x 1 x 300 mm² | 4 x 3 x 1 x 400 mm²
Current Rating (Base) as per IEC 61892-4 Annex A, Table A-7 | [7 empty] | 37 | 47 | 65 | 87 | 110 | 137 | 167 | 214 | 259 | 301 | 347 | 397 | 468 | 386 | 444 | 528 | 612 | 716 | 772 | 888 | 1056 | 1224 | 1432 | 1584 | 1836 | 2148 | 2112 | 2448 | 2864
Derating factor | [7 empty] | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945
Current Rating (Derated) | [7 empty] | 24.2424 | 30.7944 | 42.588 | 57.0024 | 72.072 | 89.7624 | 109.4184 | 140.2128 | 169.6968 | 197.2152 | 227.3544 | 260.1144 | 306.6336 | 364.77 | 419.58 | 498.96 | 578.34 | 676.62 | 729.54 | 839.16 | 997.92 | 1156.68 | 1353.24 | 1496.88 | 1735.02 | 2029.86 | 1995.84 | 2313.36 | 2706.48
Typical Resistance (a.c. at conductor temp.) (Ω/Km) form IEC 60228 | [7 empty] | 5.9927 | 3.9654 | 2.3461 | 1.4791 | 0.93589 | 0.6745 | 0.49854 | 0.34426 | 0.24863 | 0.19636 | 0.16066 | 0.1275 | 0.097159 | 0.16066 | 0.1275 | 0.097159 | 0.077395 | 0.059927 | 0.080328 | 0.063752 | 0.048579 | 0.038698 | 0.029964 | 0.032386 | 0.025798 | 0.019976 | 0.02429 | 0.019349 | 0.014982
Reactance at 50Hz (Ω/Km) | [7 empty] | 0.096 | 0.091 | 0.085 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.073 | 0.073 | 0.072 | 0.094 | 0.093 | 0.09 | 0.089 | 0.086 | 0.047 | 0.0465 | 0.045 | 0.0445 | 0.043 | 0.03 | 0.029667 | 0.028667 | 0.0225 | 0.02225 | 0.0215
V | Motor Rating (KW) | Efficiency | F.L.C (A) | Power Factor | Is/In | L.R.C. (A) | L.R. Power Factor | MAXIMUM ROUTE LENGTH (METERS)
400 | 0.55 | 75.4% | 1.3853 | 0.76 | 4.9 | 6.7882 | 0.75 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 0.75 | 80.4% | 1.7716 | 0.76 | 5.2 | 9.2124 | 0.75 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 1.1 | 81.8% | 2.3963 | 0.81 | 5.9 | 14.1379 | 0.72 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 1.5 | 83.2% | 3.294 | 0.79 | 6.5 | 21.4108 | 0.78 | 341.7367 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 2.2 | 84.7% | 4.3593 | 0.86 | 7 | 30.5153 | 0.74 | 252.312 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 3 | 85.7% | 6.0875 | 0.83 | 7 | 42.6128 | 0.55 | 240.7829 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 4 | 86.9% | 8.7419 | 0.76 | 8.3 | 72.5578 | 0.59 | 132.1332 | 197.851 | 328.62 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 5.5 | 87.7% | 11.4582 | 0.79 | 7 | 80.2072 | 0.48 | 145.8742 | 217.7736 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 7.5 | 89.1% | 16.1995 | 0.75 | 6.8 | 110.1566 | 0.52 | 98.3268 | 146.9668 | 243.2907 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 11 | 91.2% | 21.2307 | 0.82 | 7.8 | 165.5991 | 0.55 | 61.9594 | 92.6844 | 153.662 | 237.4066 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 15 | 92% | 28.0158 | 0.84 | 7.8 | 218.5235 | 0.57 | NOK | 67.8885 | 112.6585 | 174.2748 | 264.5638 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 18.5 | 91.6% | 35.1219 | 0.83 | 7.2 | 252.8774 | 0.56 | NOK | NOK | 98.9627 | 152.9936 | 232.0343 | 309.6859 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 22 | 91.6% | 41.7665 | 0.83 | 6.8 | 284.0125 | 0.39 | NOK | NOK | 122.7996 | 187.2377 | 278.051 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 30 | 93.6% | 54.4259 | 0.85 | 7.4 | 402.7519 | 0.39 | NOK | NOK | NOK | 132.0362 | 196.0759 | 256.8415 | 324.1593 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 37 | 93.6% | 67.1253 | 0.85 | 7.6 | 510.1524 | 0.36 | NOK | NOK | NOK | NOK | 164.9919 | 215.1625 | 270.1938 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 45 | 94.14% | 78.4034 | 0.88 | 7.6 | 595.866 | 0.36 | NOK | NOK | NOK | NOK | NOK | 184.212 | 231.3272 | 299.8129 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 55 | 94.3% | 100.2192 | 0.84 | 7.2 | 721.5785 | 0.37 | NOK | NOK | NOK | NOK | NOK | NOK | 187.5308 | 243.624 | 298.6583 | 341.7578 | >350 | >350 | >350 | 327.0879 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 75 | 94.5% | 134.769 | 0.85 | 6.9 | 929.9059 | 0.37 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 189.0448 | 231.7497 | 265.1936 | 292.7201 | 323.9428 | >350 | 253.8102 | 278.8821 | 311.5731 | 334.64 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 90 | 94.7% | 159.5047 | 0.86 | 7.2 | 1148.4338 | 0.37 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 187.6516 | 214.7317 | 237.0203 | 262.3019 | 293.3099 | 205.5143 | 225.8155 | 252.2859 | 270.9635 | 295.5203 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 110 | 95.1% | 194.1302 | 0.86 | 7.2 | 1397.7374 | 0.37 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 176.4316 | 194.7448 | 215.5171 | 240.9945 | 168.8583 | 185.5385 | 207.2876 | 222.6339 | 242.8106 | 337.7167 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 132 | 95.4% | 232.2237 | 0.86 | 7.1 | 1648.7881 | 0.35 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 185.9135 | 207.0938 | 145.6154 | 159.4753 | 177.5797 | 190.206 | 206.9235 | 291.2307 | 318.9506 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350 | >350
400 | 160 | 95.6% | 284.199 | 0.85 | 7.2 | 2046.2328 | 0.35 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 166.8695 | 117.3321 | 128.5 | 143.0879 | 153.2618 | 166.7323 | 234.6643 | 257.0001 | 286.1759 | 306.5236 | 333.4645 | >350 | >350 | >350 | >350 | >350 | >350
400 | 200 | 95.6% | 351.118 | 0.86 | 7.2 | 2528.0492 | 0.35 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 94.97 | 104.0094 | 115.8171 | 124.0519 | 134.9551 | 189.94 | 208.0189 | 231.6341 | 248.1038 | 269.9101 | 347.4512 | >350 | >350 | >350 | >350 | >350
400 | 250 | 95.9% | 437.5245 | 0.86 | 7.1 | 3106.4236 | 0.3 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 96.967 | 103.14 | 111.4952 | 161.7704 | 175.6573 | 193.934 | 206.2799 | 222.9905 | 290.901 | 309.4199 | 334.4857 | >350 | >350 | >350
400 | 315 | 95.9% | 551.2808 | 0.86 | 7.3 | 4024.3499 | 0.3 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 79.6145 | 86.0639 | 124.8717 | 135.5911 | 149.699 | 159.2289 | 172.1279 | 224.5485 | 238.8434 | 258.1918 | 299.398 | 318.4578 | 344.2558
400 | 350 | 95.9% | 612.5342 | 0.86 | 6.9 | 4226.4862 | 0.3 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 81.9478 | 118.8996 | 129.1063 | 142.5395 | 151.6136 | 163.8957 | 213.8092 | 227.4204 | 245.8435 | 285.079 | 303.2272 | 327.7914
400 | 400 | 96.3% | 705.3329 | 0.85 | 6.8 | 4796.2639 | 0.3 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 104.7748 | 113.769 | 125.6063 | 133.6025 | 144.4255 | 188.4095 | 200.4038 | 216.6382 | 251.2127 | 267.205 | 288.851
400 | 450 | 96.9% | 779.4166 | 0.86 | 6.9 | 5377.9747 | 0.3 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 101.4631 | 112.0201 | 119.1513 | 128.8037 | 168.0301 | 178.727 | 193.2055 | 224.0402 | 238.3027 | 257.6073
400 | 500 | 97% | 865.1257 | 0.86 | 6.8 | 5882.8546 | 0.3 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 102.4063 | 108.9255 | 117.7494 | 153.6094 | 163.3882 | 176.6242 | 204.8125 | 217.851 | 235.4989
Note on F6: For display only

## Sheet1
Ref | Power | Lenght | Result Size
titi | 132 | 350 | 3 x 185 mm²
toto | 30 | 44 | 3 x 16 mm²
tata | 7.5 | 220
tautau | 9.5 | 50
tutu | 350 | 350
toutou | 12 | 68
tyty | 3 | 280

## LV FEEDER CHART IN AIR
LV FEEDERS - CABLES LAID IN AIR
Maximum Volt Drop at LV bus (%) |  |  | ΔVb | 5% |  | DERATING FACTORS | Ambient temperature factor (40°C) |  |  |  |  | 1.05
[7 empty] | Layer factor |  |  |  |  | 0.8
Max Length |  |  | Lmax | 500 |  |  | Touching - LV 3-core |  |  |  |  | 0.78
[7 empty] | Trefoil untouching - LV single core |  |  |  |  | 0.9
|  |  | 3-CORE CABLES | [12 empty] | SINGLE-CORE CABLES
Conductor Size |  |  | 3 x 4 mm² | 3 x 6 mm² | 3 x 10 mm² | 3 x 16 mm² | 3 x 25 mm² | 3 x 35 mm² | 3 x 50 mm² | 3 x 70 mm² | 3 x 95 mm² | 3 x 120 mm² | 3 x 150 mm² | 3 x 185 mm² | 3 x 240 mm² | 3 x 1 x 150 mm² | 3 x 1 x 185 mm² | 3 x 1 x 240 mm² | 3 x 1 x 300 mm² | 3 x 1 x 400 mm² | 2 x 3 x 1 x 150 mm² | 2 x 3 x 1 x 185 mm² | 2 x 3 x 1 x 240 mm² | 2 x 3 x 1 x 300 mm² | 2 x 3 x 1 x 400 mm² | 3 x 3 x 1 x 240 mm² | 3 x 3 x 1 x 300 mm² | 3 x 3 x 1 x 400 mm² | 3 x 3 x 1 x 500 mm² | 3 x 3 x 1 x 630 mm² | 4 x 3 x 1 x 240 mm² | 4 x 3 x 1 x 300 mm² | 4 x 3 x 1 x 400 mm² | 4 x 3 x 1 x 500 mm² | 4 x 3 x 1 x 630 mm² | 5 x 3 x 1 x 240 mm² | 5 x 3 x 1 x 300 mm² | 5 x 3 x 1 x 400 mm² | 5 x 3 x 1 x 500 mm² | 5 x 3 x 1 x 630 mm² | 6 x 3 x 1 x 240 mm² | 6 x 3 x 1 x 300 mm² | 6 x 3 x 1 x 400 mm² | 6 x 3 x 1 x 500 mm² | 6 x 3 x 1 x 630 mm²
Current Rating (Base) as per IEC 61892-4 Annex A, Table A-7 |  |  | 37 | 47 | 65 | 87 | 110 | 137 | 167 | 214 | 259 | 301 | 347 | 397 | 468 | 386 | 444 | 528 | 612 | 716 | 772 | 888 | 1056 | 1224 | 1432 | 1584 | 1836 | 2148 | 2469 | 2841 | 2112 | 2448 | 2864 | 3292 | 3788 | 2640 | 3060 | 3580 | 4115 | 4735 | 3168 | 3672 | 4296 | 4938 | 5682
Derating factor |  |  | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945
Current Rating (Derated) |  |  | 24.2424 | 30.7944 | 42.588 | 57.0024 | 72.072 | 89.7624 | 109.4184 | 140.2128 | 169.6968 | 197.2152 | 227.3544 | 260.1144 | 306.6336 | 364.77 | 419.58 | 498.96 | 578.34 | 676.62 | 729.54 | 839.16 | 997.92 | 1156.68 | 1353.24 | 1496.88 | 1735.02 | 2029.86 | 2333.205 | 2684.745 | 1995.84 | 2313.36 | 2706.48 | 3110.94 | 3579.66 | 2494.8 | 2891.7 | 3383.1 | 3888.675 | 4474.575 | 2993.76 | 3470.04 | 4059.72 | 4666.41 | 5369.49
Typical Resistance (a.c. at conductor temp.) (Ω/Km) form IEC 60228 |  |  | 5.9927 | 3.9654 | 2.3461 | 1.4791 | 0.93589 | 0.6745 | 0.49854 | 0.34426 | 0.24863 | 0.19636 | 0.16066 | 0.1275 | 0.097159 | 0.16066 | 0.1275 | 0.097159 | 0.077395 | 0.059927 | 0.080328 | 0.063752 | 0.048579 | 0.038698 | 0.029964 | 0.032386 | 0.025798 | 0.019976 | 0.015556 | 0.012028 | 0.02429 | 0.019349 | 0.014982 | 0.011667 | 0.009021 | 0.019432 | 0.015479 | 0.011985 | 0.0093334 | 0.0072168 | 0.016193 | 0.012899 | 0.0099879 | 0.0077778 | 0.006014
Reactance at 50Hz (Ω/Km) |  |  | 0.096 | 0.091 | 0.085 | 0.081 | 0.08 | 0.078 | 0.077 | 0.075 | 0.074 | 0.073 | 0.073 | 0.073 | 0.072 | 0.094 | 0.093 | 0.09 | 0.089 | 0.086 | 0.047 | 0.0465 | 0.045 | 0.0445 | 0.043 | 0.03 | 0.029667 | 0.028667 | 0.028333 | 0.012 | 0.0225 | 0.02225 | 0.0215 | 0.02125 | 0.009 | 0.018 | 0.0178 | 0.0172 | 0.017 | 0.0072 | 0.015 | 0.014833 | 0.014333 | 0.014167 | 0.006
V | F.L.C (A) | Power Factor | MAXIMUM ROUTE LENGTH (METERS)
400 | 16 | 0.85 | 140.2863 | 211.1106 | 353.9501 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 20 | 0.85 | 112.2291 | 168.8885 | 283.1601 | 444.1608 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 25 | 0.85 | NOK | 135.1108 | 226.5281 | 355.3286 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 31.5 | 0.85 | NOK | NOK | 179.7842 | 282.0068 | 437.6213 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 40 | 0.85 | NOK | NOK | 141.5801 | 222.0804 | 344.6267 | 469.8375 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 50 | 0.85 | NOK | NOK | NOK | 177.6643 | 275.7014 | 375.87 | 497.3675 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 63 | 0.85 | NOK | NOK | NOK | NOK | 218.8106 | 298.3095 | 394.7361 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 80 | 0.85 | NOK | NOK | NOK | NOK | NOK | 234.9187 | 310.8547 | 434.5783 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 100 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | 248.6838 | 347.6626 | 461.2874 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 125 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 278.1301 | 369.0299 | 449.827 | >500 | >500 | >500 | 496.4443 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 160 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 288.3046 | 351.4273 | 412.3627 | 491.4981 | >500 | 387.8471 | 458.5931 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 200 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 329.8901 | 393.1985 | 479.076 | 310.2777 | 366.8745 | 444.1314 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 250 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 314.5588 | 383.2608 | 248.2222 | 293.4996 | 355.3051 | 409.9414 | 479.9178 | 496.4443 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 315 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 197.0017 | 232.9362 | 281.9882 | 325.3503 | 380.8872 | 394.0034 | 465.8724 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 400 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 183.4372 | 222.0657 | 256.2134 | 299.9486 | 310.2777 | 366.8745 | 444.1314 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 500 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 204.9707 | 239.9589 | 248.2222 | 293.4996 | 355.3051 | 409.9414 | 479.9178 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 630 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 190.4436 | 197.0017 | 232.9362 | 281.9882 | 325.3503 | 380.8872 | 422.9823 | 488.0255 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 800 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 183.4372 | 222.0657 | 256.2134 | 299.9486 | 333.0985 | 384.32 | 449.923 | >500 | >500 | 444.1314 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 1000 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 204.9707 | 239.9589 | 266.4788 | 307.456 | 359.9384 | 410.2281 | >500 | 355.3051 | 409.9414 | 479.9178 | >500 | >500 | 444.1314 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500 | >500
400 | 1250 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 191.9671 | 213.1831 | 245.9648 | 287.9507 | 328.1825 | >500 | 284.2441 | 327.9531 | 383.9343 | 437.5766 | >500 | 355.3051 | 409.9414 | 479.9178 | >500 | >500 | 426.3661 | 491.9297 | >500 | >500 | >500
400 | 1600 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 192.16 | 224.9615 | 256.3926 | 436.1927 | 222.0657 | 256.2134 | 299.9486 | 341.8567 | >500 | 277.5821 | 320.2667 | 374.9358 | 427.3209 | >500 | 333.0985 | 384.32 | 449.923 | >500 | >500
400 | 2000 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 179.9692 | 205.114 | 348.9542 | NOK | 204.9707 | 239.9589 | 273.4854 | 465.2722 | 222.0657 | 256.2134 | 299.9486 | 341.8567 | >500 | 266.4788 | 307.456 | 359.9384 | 410.2281 | >500
400 | 2500 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 279.1633 | NOK | NOK | 191.9671 | 218.7883 | 372.2178 | NOK | 204.9707 | 239.9589 | 273.4854 | 465.2722 | 213.1831 | 245.9648 | 287.9507 | 328.1825 | >500
400 | 3150 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 295.4109 | NOK | NOK | 190.4436 | 217.0519 | 369.2637 | NOK | 195.2102 | 228.5323 | 260.4623 | 443.1164
400 | 4000 | 0.85 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 290.7951 | NOK | NOK | 179.9692 | 205.114 | 348.9542
Note on F6: For display only

## DC FEEDER CHART IN AIR
DC FEEDERS - CABLES LAID IN AIR
Maximum Volt Drop at LV bus (%) |  | ΔVb | 2% |  | DERATING FACTORS | Ambient temperature factor (40°C) |  |  |  |  | 1.05
[6 empty] | Layer factor |  |  |  |  | 0.8
Max Length |  | Lmax | 100 |  |  | Touching - LV |  |  |  |  | 0.78
[14 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
SINGLE-CORE CABLES
Conductor Size |  | 1 x 10 mm² | 1 x 16 mm² | 1 x 25 mm² | 1 x 35 mm² | 1 x 50 mm² | 1 x 70 mm² | 1 x 95 mm² | 1 x 120 mm² | 1 x 150 mm² | 1 x 185 mm² | 1 x 240 mm² | 1 x 300 mm² | 2 x 1 x 10 mm² | 2 x 1 x 16 mm² | 2 x 1 x 25 mm² | 2 x 35 mm² | 2 x 1 x 50 mm² | 2 x 1 x 70 mm² | 2 x 1 x 95 mm² | 2 x 1 x 120 mm² | 2 x 1 x 150 mm² | 2 x 1 x 185 mm² | 2 x 1 x 240 mm² | 2 x 1 x 300 mm² | 3 x 1 x 10 mm² | 3 x 1 x 16 mm² | 3 x 1 x 25 mm² | 2 x 35 mm² | 3 x 1 x 50 mm² | 3 x 1 x 70 mm² | 3 x 1 x 95 mm² | 3 x 1 x 120 mm² | 3 x 1 x 150 mm² | 3 x 1 x 185 mm² | 3 x 1 x 240 mm² | 3 x 1 x 300 mm²
Current Rating (Base) as per IEC 61892-4 Annex A, Table A-7 |  | 70 | 93 | 117 | 147 | 180 | 233 | 285 | 333 | 386 | 444 | 528 | 612 | 140 | 186 | 234 | 294 | 360 | 466 | 570 | 666 | 772 | 888 | 1056 | 1224 | 210 | 279 | 351 | 441 | 540 | 699 | 855 | 999 | 1158 | 1332 | 1584 | 1836
Derating factor |  | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552 | 0.6552
Current Rating (Derated) |  | 45.864 | 60.9336 | 76.6584 | 96.3144 | 117.936 | 152.6616 | 186.732 | 218.1816 | 252.9072 | 290.9088 | 345.9456 | 400.9824 | 91.728 | 121.8672 | 153.3168 | 192.6288 | 235.872 | 305.3232 | 373.464 | 436.3632 | 505.8144 | 581.8176 | 691.8912 | 801.9648 | 137.592 | 182.8008 | 229.9752 | 288.9432 | 353.808 | 457.9848 | 560.196 | 654.5448 | 758.7216 | 872.7264 | 1037.8368 | 1202.9472
Typical Resistance (at conductor temp.) (Ω/Km) form IEC 60228 |  | 2.3461 | 1.4791 | 0.93589 | 0.6745 | 0.49854 | 0.34426 | 0.24863 | 0.19636 | 0.16066 | 0.1275 | 0.097159 | 0.077395 | 1.173 | 0.73953 | 0.46794 | 0.33725 | 0.24927 | 0.17213 | 0.12432 | 0.098179 | 0.080328 | 0.063752 | 0.048579 | 0.038698 | 0.78203 | 0.49302 | 0.31196 | 0.22483 | 0.16618 | 0.11475 | 0.082878 | 0.065453 | 0.053552 | 0.042502 | 0.032386 | 0.025798
V | F.L.C (A) | MAXIMUM ROUTE LENGTH (METERS)
48 | 16 | 12.7872 | 20.2832 | 32.0552 | 44.4773 | 60.1752 | 87.1426 | >100 | >100 | >100 | >100 | >100 | >100 | 25.5745 | 40.5664 | 64.1104 | 88.9547 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | 38.3617 | 60.8496 | 96.1656 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | >100
48 | 20 | 10.2298 | 16.2266 | 25.6441 | 35.5819 | 48.1402 | 69.7141 | 96.5272 | >100 | >100 | >100 | >100 | >100 | 20.4596 | 32.4531 | 51.2883 | 71.1637 | 96.2803 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | 30.6894 | 48.6797 | 76.9324 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | >100
48 | 25 | 8.1838 | 12.9812 | 20.5153 | 28.4655 | 38.5121 | 55.7713 | 77.2218 | 97.7808 | >100 | >100 | >100 | >100 | 16.3677 | 25.9625 | 41.0306 | 56.931 | 77.0243 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | 24.5515 | 38.9437 | 61.546 | 85.3965 | >100 | >100 | >100 | >100 | >100 | >100 | >100 | >100
48 | 31.5 | 6.4951 | 10.3026 | 16.282 | 22.5917 | 30.5652 | 44.2629 | 61.2871 | 77.6038 | 94.8491 | >100 | >100 | >100 | 12.9902 | 20.6051 | 32.564 | 45.1833 | 61.1304 | 88.5258 | >100 | >100 | >100 | >100 | >100 | >100 | 19.4853 | 30.9077 | 48.846 | 67.775 | 91.6956 | >100 | >100 | >100 | >100 | >100 | >100 | >100
48 | 40 | 5.1149 | 8.1133 | 12.8221 | 17.7909 | 24.0701 | 34.857 | 48.2636 | 61.113 | 74.6937 | 94.114 | >100 | >100 | 10.2298 | 16.2266 | 25.6441 | 35.5819 | 48.1402 | 69.7141 | 96.5272 | >100 | >100 | >100 | >100 | >100 | 15.3447 | 24.3398 | 38.4662 | 53.3728 | 72.2102 | >100 | >100 | >100 | >100 | >100 | >100 | >100
48 | 50 | NOK | 6.4906 | 10.2577 | 14.2327 | 19.2561 | 27.8856 | 38.6109 | 48.8904 | 59.7549 | 75.2912 | 98.8074 | >100 | 8.1838 | 12.9812 | 20.5153 | 28.4655 | 38.5121 | 55.7713 | 77.2218 | 97.7808 | >100 | >100 | >100 | >100 | 12.2757 | 19.4719 | 30.773 | 42.6982 | 57.7682 | 83.6569 | >100 | >100 | >100 | >100 | >100 | >100
48 | 63 | NOK | NOK | 8.141 | 11.2958 | 15.2826 | 22.1315 | 30.6436 | 38.8019 | 47.4246 | 59.7549 | 78.4185 | 98.4431 | 6.4951 | 10.3026 | 16.282 | 22.5917 | 30.5652 | 44.2629 | 61.2871 | 77.6038 | 94.8491 | >100 | >100 | >100 | 9.7427 | 15.4539 | 24.423 | 33.8875 | 45.8478 | 66.3944 | 91.9307 | >100 | >100 | >100 | >100 | >100
48 | 80 | NOK | NOK | NOK | 8.8955 | 12.035 | 17.4285 | 24.1318 | 30.5565 | 37.3468 | 47.057 | 61.7546 | 77.5239 | 5.1149 | 8.1133 | 12.8221 | 17.7909 | 24.0701 | 34.857 | 48.2636 | 61.113 | 74.6937 | 94.114 | >100 | >100 | 7.6723 | 12.1699 | 19.2331 | 26.6864 | 36.1051 | 52.2856 | 72.3954 | 91.6695 | >100 | >100 | >100 | >100
48 | 100 | NOK | NOK | NOK | NOK | 9.628 | 13.9428 | 19.3054 | 24.4452 | 29.8775 | 37.6456 | 49.4037 | 62.0191 | NOK | 6.4906 | 10.2577 | 14.2327 | 19.2561 | 27.8856 | 38.6109 | 48.8904 | 59.7549 | 75.2912 | 98.8074 | >100 | 6.1379 | 9.7359 | 15.3865 | 21.3491 | 28.8841 | 41.8285 | 57.9163 | 73.3356 | 89.6324 | >100 | >100 | >100
48 | 125 | NOK | NOK | NOK | NOK | NOK | 11.1543 | 15.4444 | 19.5562 | 23.902 | 30.1165 | 39.5229 | 49.6153 | NOK | NOK | 8.2061 | 11.3862 | 15.4049 | 22.3085 | 30.8887 | 39.1123 | 47.8039 | 60.233 | 79.0459 | 99.2306 | 4.9103 | 7.7887 | 12.3092 | 17.0793 | 23.1073 | 33.4628 | 46.3331 | 58.6685 | 71.7059 | 90.3495 | >100 | >100
48 | 160 | NOK | NOK | NOK | NOK | NOK | NOK | 12.0659 | 15.2783 | 18.6734 | 23.5285 | 30.8773 | 38.762 | NOK | NOK | NOK | 8.8955 | 12.035 | 17.4285 | 24.1318 | 30.5565 | 37.3468 | 47.057 | 61.7546 | 77.5239 | NOK | 6.085 | 9.6166 | 13.3432 | 18.0526 | 26.1428 | 36.1977 | 45.8348 | 56.0203 | 70.5855 | 92.6319 | >100
48 | 200 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 12.2226 | 14.9387 | 18.8228 | 24.7018 | 31.0096 | NOK | NOK | NOK | NOK | 9.628 | 13.9428 | 19.3054 | 24.4452 | 29.8775 | 37.6456 | 49.4037 | 62.0191 | NOK | NOK | 7.6932 | 10.6746 | 14.442 | 20.9142 | 28.9582 | 36.6678 | 44.8162 | 56.4684 | 74.1055 | 93.0287
48 | 250 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 11.951 | 15.0582 | 19.7615 | 24.8076 | NOK | NOK | NOK | NOK | NOK | 11.1543 | 15.4444 | 19.5562 | 23.902 | 30.1165 | 39.5229 | 49.6153 | NOK | NOK | NOK | 8.5396 | 11.5536 | 16.7314 | 23.1665 | 29.3342 | 35.853 | 45.1747 | 59.2844 | 74.4229
48 | 315 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 15.6837 | 19.6886 | NOK | NOK | NOK | NOK | NOK | NOK | 12.2574 | 15.5208 | 18.9698 | 23.902 | 31.3674 | 39.3772 | NOK | NOK | NOK | NOK | 9.1696 | 13.2789 | 18.3861 | 23.2811 | 28.4547 | 35.853 | 47.0511 | 59.0658
48 | 400 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 15.5048 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 12.2226 | 14.9387 | 18.8228 | 24.7018 | 31.0096 | NOK | NOK | NOK | NOK | NOK | 10.4571 | 14.4791 | 18.3339 | 22.4081 | 28.2342 | 37.0528 | 46.5143
48 | 500 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 11.951 | 15.0582 | 19.7615 | 24.8076 | NOK | NOK | NOK | NOK | NOK | NOK | 11.5833 | 14.6671 | 17.9265 | 22.5874 | 29.6422 | 37.2115
48 | 630 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 15.6837 | 19.6886 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 11.6406 | 14.2274 | 17.9265 | 23.5256 | 29.5329
48 | 800 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 15.5048 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 14.1171 | 18.5264 | 23.2572
48 | 1000 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | 14.8211 | 18.6057
48 | 1250 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK
48 | 1600 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK
48 | 2000 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK
48 | 2500 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK
48 | 3150 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK
48 | 4000 | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK | NOK
Note on E6: For display only

## ABB MOTOR DATA Ex na
ABB LV 690V, 50Hz, 1500rpm, Ex na IIB/IIC, IP55, IC 411, Insulation class F, temperature rise class B, IE2
Number of poles | Voltage | Design | Output kW | Motor type | IEC Frame Size | Frame Type | Speed | Efficiency at |  | Power factor | Current |  | Torque |  |  | Moment of inertia | Weight | Sound pressure level LP | Max.conn cable area
|  |  | 50 Hz |  |  |  | r/min | FL | 3/4 | cos phi | IN | IS/IN | TN | TS/TN | Tmax/TN | J=1/4GD2 | Ex na
| V | [6 empty] | 100% | 75% |  | A |  | Nm |  |  | kgm2 | kg | dB(A) | mm2
4 poles | 690 | Basic | 0.55 | M3GP 80 MA |  |  | 1421 | 75.4% | 75.4% | 0.76 | 1.38 | 4.9 | 3.6 | 2.3 | 2.7 | 0.001 | 38 | 59
4 poles | 690 | Basic | 0.75 | M3GP 80 MB |  |  | 1412 | 80.4% | 80.5% | 0.76 | 1.77 | 5.2 | 5 | 2.2 | 2.7 | 0.0012 | 38 | 59
4 poles | 690 | Basic | 1.1 | M3GP 90 SLA |  |  | 1435 | 81.8% | 81.8% | 0.81 | 2.3 | 5.9 | 7.3 | 2.8 | 3.5 | 0.002 | 51 | 54
4 poles | 690 | Basic | 1.5 | M3GP 90 SLC |  |  | 1431 | 83.2% | 28.8% | 0.79 | 3.2 | 6.5 | 10 | 2.3 | 3 | 0.003 | 53 | 54
4 poles | 690 | Basic | 2.2 | M3GP 100 LA |  |  | 1441 | 84.7% | 85.6% | 0.86 | 4.3 | 7 | 14.5 | 2.7 | 3.3 | 0.0075 | 61 | 52
4 poles | 690 | Basic | 3 | M3GP 100 LB |  |  | 1442 | 85.7% | 86.5% | 0.83 | 6 | 7 | 19.8 | 2.7 | 3.4 | 0.0081 | 63 | 52
4 poles | 690 | Basic | 4 | M3GP 112 MC |  |  | 1455 | 86.9% | 86.4% | 0.76 | 8.7 | 8.3 | 26.2 | 3 | 3.8 | 0.013 | 72 | 52
4 poles | 690 | Basic | 5.5 | M3GP 132 SMB |  |  | 1458 | 87.7% | 87.8% | 0.79 | 11.4 | 7 | 36 | 3 | 3.5 | 0.023 | 102 | 60
4 poles | 690 | Basic | 7.5 | M3GP 132 SMD |  |  | 1460 | 89.1% | 89.1% | 0.75 | 16.1 | 6.8 | 49 | 3.3 | 3.7 | 0.034 | 111 | 60
4 poles | 690 | Basic | 11 | M3GP 160 MLC |  |  | 1470 | 91.2% | 91.5% | 0.82 | 21.2 | 7.8 | 71.4 | 3 | 3.5 | 0.096 | 226 | 62
4 poles | 690 | Basic | 15 | M3GP 160 MLE |  |  | 1467 | 92% | 92.4% | 0.84 | 28 | 7.8 | 97.6 | 3 | 3.4 | 0.13 | 249 | 61
4 poles | 690 | Basic | 18.5 | M3GP 180 MLA |  |  | 1474 | 91.6% | 92% | 0.83 | 35.1 | 7.2 | 119.6 | 2.6 | 3.1 | 0.19 | 271 | 62
4 poles | 690 | Basic | 22 | M3GP 180 MLB |  |  | 1471 | 91.6% | 92.4% | 0.83 | 41.7 | 6.8 | 142 | 2.5 | 3 | 0.21 | 279 | 62
4 poles | 690 | Basic | 30 | M3GP 200 MLB |  |  | 1475 | 93.6% | 94% | 0.85 | 54.4 | 7.4 | 194 | 3 | 2.8 | 0.34 | 305 | 61
4 poles | 690 | Basic | 37 | M3GP 225 SMB |  |  | 1480 | 93.6% | 93.9% | 0.85 | 67.1 | 7.6 | 238 | 3.2 | 2.9 | 0.42 | 355 | 67
4 poles | 690 | Basic | 45 | M3GP 225 SMC |  |  | 1477 | 94.14% | 94.6% | 0.88 | 78.4 | 7.6 | 290 | 3.2 | 2.7 | 0.49 | 390 | 67
4 poles | 690 | Basic | 55 | M3GP 250 SMA |  |  | 1479 | 94.3% | 94.3% | 0.84 | 100 | 7.2 | 355 | 2.5 | 3.1 | 0.72 | 415 | 66
4 poles | 690 | Basic | 75 | M3GP 280 SMA |  |  | 1484 | 94.5% | 94.5% | 0.85 | 134 | 6.9 | 482 | 2.5 | 2.8 | 1.25 | 625 | 68
4 poles | 690 | Basic | 90 | M3GP 280 SMB |  |  | 1483 | 94.7% | 94.8% | 0.86 | 159 | 7.2 | 579 | 2.5 | 2.7 | 1.5 | 665 | 68
4 poles | 690 | Basic | 110 | M3GP 315 SMA |  |  | 1487 | 95.1% | 95.1% | 0.86 | 194 | 7.2 | 706 | 2 | 2.5 | 2.3 | 900 | 70
4 poles | 690 | Basic | 132 | M3GP 315 SMB |  |  | 1487 | 95.4% | 95.4% | 0.86 | 232 | 7.1 | 847 | 2.3 | 2.7 | 2.6 | 960 | 70
4 poles | 690 | Basic | 160 | M3GP 315 SMC |  |  | 1487 | 95.6% | 95.6% | 0.85 | 284 | 7.2 | 1027 | 2.4 | 2.9 | 2.9 | 1000 | 70
4 poles | 690 | Basic | 200 | M3GP 315 MLA |  |  | 1486 | 95.6% | 95.6% | 0.86 | 351 | 7.2 | 1285 | 2.5 | 2.9 | 3.5 | 1160 | 74
4 poles | 690 | Basic | 250 | M3GP 355 SMA |  |  | 1488 | 95.9% | 95.9% | 0.86 | 437 | 7.1 | 1604 | 2.3 | 2.7 | 5.9 | 1610 | 74
4 poles | 690 | Basic | 315 | M3GP 355 SMB |  |  | 1488 | 95.9% | 95.9% | 0.86 | 551 | 7.3 | 2021 | 2.3 | 2.8 | 6.9 | 1780 | 74
4 poles | 690 | Basic | 350 | M3GP 355 SMC |  |  | 1487 | 95.9% | 95.9% | 0.86 | 612 | 6.9 | 2247 | 2.4 | 2.7 | 7.2 | 1820 | 78
4 poles | 690 | Basic | 400 | M3GP 355 MLA |  |  | 1489 | 96.3% | 96.3% | 0.85 | 705 | 6.8 | 2565 | 2.3 | 2.6 | 8.4 | 2140 | 78
4 poles | 690 | Basic | 450 | M3GP 355 MLB |  |  | 1490 | 96.9% | 96.8% | 0.86 | 780 | 6.9 | 2884 | 2.3 | 2.9 | 8.4 | 2140 | 78
4 poles | 690 | Basic | 500 | M3GP 355 LKA |  |  | 1490 | 97% | 97% | 0.86 | 865 | 6.8 | 3204 | 2 | 3 | 10 | 2500 | 78
4 poles | 690 | Basic | 560 | M3GP 400 LA |  |  | 1491 | 96.8% | 96.8% | 0.85 | 982 | 7.4 | 3586 | 2.4 | 2.8 | 15 | 3200 | 78
4 poles | 690 | Basic | 560 | M3GP 400 LKA |  |  | 1491 | 96.8% | 96.8% | 0.85 | 982 | 7.4 | 3586 | 2.4 | 2.8 | 15 | 3200 | 78
4 poles | 690 | Basic | 630 | M3GP 400 LB |  |  | 1491 | 97% | 97% | 0.87 | 1077 | 7.6 | 4034 | 2.2 | 2.9 | 16 | 3300 | 78
4 poles | 690 | Basic | 630 | M3GP 400 LKB |  |  | 1491 | 97% | 97% | 0.87 | 1077 | 4.6 | 4034 | 2.2 | 2.9 | 16 | 3300 | 78
4 poles | 690 | Basic | 680 | M3GP 400 LC |  |  | 1492 | 97.1% | 97.1% | 0.85 | 1189 | 7.9 | 4352 | 2.5 | 3.1 | 17 | 3400 | 78
4 poles | 690 | Basic | 680 | M3GP 400 LKC |  |  | 1492 | 97.1% | 97.1% | 0.85 | 1189 | 7.9 | 4352 | 2.5 | 3.1 | 17 | 3400 | 78
4 poles | 690 | Basic | 800 | M3GP 450 LA |  |  | 1492 | 96.9% | 96.9% | 0.86 | 1385 | 7 | 5120 | 1.3 | 2.8 | 23 | 4050 | 85
4 poles | 690 | Basic | 900 | M3GP 450 LB |  |  | 1492 | 97.1% | 97.1% | 0.86 | 1555 | 7 | 5760 | 1.3 | 2.8 | 25 | 4350 | 85
4 poles | 690 | Basic | 1000 | M3GP 450 LC |  |  | 1491 | 97.2% | 97.2% | 0.86 | 1726 | 6.8 | 6404 | 1.3 | 2.7 | 30 | 4700 | 85
4 poles | 690 | High Output | 18.5 | M3GP 160 MLF |  |  | 1469 | 91.7% | 92.1% | 0.83 | 35 | 7.8 | 120 | 3.2 | 3.5 | 0.13 | 249 | 68
4 poles | 690 | High Output | 22 | M3GP 160 MLG |  |  | 1466 | 90.8% | 91.1% | 0.81 | 43.1 | 7.9 | 143 | 3.3 | 3.6 | 0.13 | 249 | 68
4 poles | 690 | High Output | 30 | M3GP 180 MLC |  |  | 1473 | 92.2% | 92.3% | 0.81 | 57.9 | 7.1 | 194 | 2.8 | 3.2 | 0.248 | 298 | 66
4 poles | 690 | High Output | 37 | M3GP 200 MLC |  |  | 1475 | 93% | 93.1% | 0.82 | 70 | 7.5 | 239 | 3.5 | 3.2 | 0.34 | 305 | 73
4 poles | 690 | High Output | 55 | M3GP 225 SMD |  |  | 1483 | 94.3% | 94.5% | 0.83 | 101 | 7.4 | 354 | 3.4 | 2.9 | 0.55 | 410 | 68
4 poles | 690 | High Output | 60 | M3GP 225 SME |  |  | 1479 | 93.6% | 93.7% | 0.84 | 110 | 8 | 387 | 3.6 | 3 | 0.55 | 410 | 74
4 poles | 690 | High Output | 75 | M3GP 250 SMB |  |  | 1476 | 94.3% | 94.5% | 0.86 | 133 | 7.6 | 485 | 2.8 | 3.2 | 0.88 | 470 | 73
4 poles | 690 | High Output | 86 | M3GP 250 SMC |  |  | 1477 | 94.1% | 94.4% | 0.85 | 155 | 7.8 | 556 | 2.9 | 3.5 | 0.98 | 495 | 74
4 poles | 690 | High Output | 110 | M3GP 280 SMC |  |  | 1485 | 95.1% | 95.2% | 0.86 | 194 | 7.6 | 707 | 3 | 3 | 1.85 | 725 | 68

## CIRCUIT PRYSMIAN
PRYSMIAN Cables according to NEK 606 III ed. 2004 & IEC 60092-300 (series)
TEOF RFOU
Designation | nb of circuit | nb of wire/circuit | nb of core/wire | Cross section core | Cable standard | Wire overall diameter approx. | Circuit overall width | Wire net weight approx. | Circuit net weight approx | Wire D.C. resistance at 20 °C max. as per IEC 60228 | Wire D.C. resistance at 90°C Correcting factor = (234,5+90)/254,5 | Circuit D.C. resistance at 90°C | Wire Current carrying capacities 45 °C free air | Circuit current carrying capacity 45°C free air | Wire Fault current at 250 °C | Circuit Fault current at 250 °C | Wire Reactance** at 50 Hz | Circuit Reactance** at 50 Hz | Wire Reactance** at 60 Hz | Wire Reactance** at 60 Hz
|  |  |  | mm² | n x mm2 | mm |  | kg/km | kg/km | Ohm/km | Ohm/km | Ohm/km | A | A | kA | kA | Ohm/km | Ohm/km | Ohm/km | Ohm/km
3 x 2,5 mm² | 1 | 1 | 3 | 2.5 | 3 x 2,5 mm² | 15.6 | 15.6 | 415 | 415 | 7.56 | 9.6394 | 9.6394 | 28 | 28 | 0.36 | 0.36 | 0.104 | 0.104 | 0.124 | 0.124
3 x 4 mm² | 1 | 1 | 3 | 4 | 3 x 4 mm² | 16.8 | 16.8 | 500 | 500 | 4.7 | 5.9927 | 5.9927 | 37 | 37 | 0.57 | 0.57 | 0.096 | 0.096 | 0.116 | 0.116
3 x 6 mm² | 1 | 1 | 3 | 6 | 3 x 6 mm² | 18.1 | 18.1 | 605 | 605 | 3.11 | 3.9654 | 3.9654 | 47 | 47 | 0.86 | 0.86 | 0.091 | 0.091 | 0.109 | 0.109
3 x 10 mm² | 1 | 1 | 3 | 10 | 3 x 10 mm² | 20.3 | 20.3 | 795 | 795 | 1.84 | 2.3461 | 2.3461 | 65 | 65 | 1.43 | 1.43 | 0.085 | 0.085 | 0.102 | 0.102
3 x 16 mm² | 1 | 1 | 3 | 16 | 3 x 16 mm² | 22.8 | 22.8 | 1125 | 1125 | 1.16 | 1.4791 | 1.4791 | 87 | 87 | 2.29 | 2.29 | 0.081 | 0.081 | 0.097 | 0.097
3 x 25 mm² | 1 | 1 | 3 | 25 | 3 x 25 mm² | 27.5 | 27.5 | 1620 | 1620 | 0.734 | 0.93589 | 0.93589 | 110 | 110 | 3.58 | 3.58 | 0.08 | 0.08 | 0.096 | 0.096
3 x 35 mm² | 1 | 1 | 3 | 35 | 3 x 35 mm² | 29.6 | 29.6 | 1955 | 1955 | 0.529 | 0.6745 | 0.6745 | 137 | 137 | 5.01 | 5.01 | 0.078 | 0.078 | 0.093 | 0.093
3 x 50 mm² | 1 | 1 | 3 | 50 | 3 x 50 mm² | 33.9 | 33.9 | 2730 | 2730 | 0.391 | 0.49854 | 0.49854 | 167 | 167 | 7.15 | 7.15 | 0.077 | 0.077 | 0.093 | 0.093
3 x 70 mm² | 1 | 1 | 3 | 70 | 3 x 70 mm² | 38.4 | 38.4 | 3655 | 3655 | 0.27 | 0.34426 | 0.34426 | 214 | 214 | 10.01 | 10.01 | 0.075 | 0.075 | 0.09 | 0.09
3 x 95 mm² | 1 | 1 | 3 | 95 | 3 x 95 mm² | 43.8 | 43.8 | 4885 | 4885 | 0.195 | 0.24863 | 0.24863 | 259 | 259 | 13.59 | 13.59 | 0.074 | 0.074 | 0.089 | 0.089
3 x 120 mm² | 1 | 1 | 3 | 120 | 3 x 120 mm² | 47.6 | 47.6 | 6000 | 6000 | 0.154 | 0.19636 | 0.19636 | 301 | 301 | 17.16 | 17.16 | 0.073 | 0.073 | 0.087 | 0.087
3 x 150 mm² | 1 | 1 | 3 | 150 | 3 x 150 mm² | 52.4 | 52.4 | 7300 | 7300 | 0.126 | 0.16066 | 0.16066 | 347 | 347 | 21.45 | 21.45 | 0.073 | 0.073 | 0.087 | 0.087
3 x 185 mm² | 1 | 1 | 3 | 185 | 3 x 185 mm² | 58.6 | 58.6 | 8960 | 8960 | 0.1 | 0.1275 | 0.1275 | 397 | 397 | 26.46 | 26.46 | 0.073 | 0.073 | 0.087 | 0.087
3 x 240 mm² | 1 | 1 | 3 | 240 | 3 x 240 mm² | 66.1 | 66.1 | 11610 | 11610 | 0.0762 | 0.097159 | 0.097159 | 468 | 468 | 34.32 | 34.32 | 0.072 | 0.072 | 0.087 | 0.087
3 x 1 x 150 mm² | 1 | 3 | 1 | 150 | 1 x 150 mm² | 26.8 | 53.6 | 2055 | 6165 | 0.126 | 0.16066 | 0.16066 | 386 | 386 | 21.45 | 21.45 | 0.094 | 0.094 | 0.113 | 0.113
3 x 1 x 185 mm² | 1 | 3 | 1 | 185 | 1 x 185 mm² | 29.3 | 58.6 | 2560 | 7680 | 0.1 | 0.1275 | 0.1275 | 444 | 444 | 26.46 | 26.46 | 0.093 | 0.093 | 0.112 | 0.112
3 x 1 x 240 mm² | 1 | 3 | 1 | 240 | 1 x 240 mm² | 32.5 | 65 | 3190 | 9570 | 0.0762 | 0.097159 | 0.097159 | 528 | 528 | 34.32 | 34.32 | 0.09 | 0.09 | 0.108 | 0.108
3 x 1 x 300 mm² | 1 | 3 | 1 | 300 | 1 x 300 mm² | 35.2 | 70.4 | 3935 | 11805 | 0.0607 | 0.077395 | 0.077395 | 612 | 612 | 42.9 | 42.9 | 0.089 | 0.089 | 0.107 | 0.107
3 x 1 x 400 mm² | 1 | 3 | 1 | 400 | 1 x 400 mm² | 0 | 0 | 0 | 0 | 0.047 | 0.059927 | 0.059927 | 0 | 0 | 42 | 42 | 0.086 | 0.086 | 0 | 0
2 x 3 x 1 x 150 mm² | 2 | 3 | 1 | 150 | 1 x 150 mm² | 26.8 | 134 | 2055 | 12330 | 0.126 | 0.16066 | 0.080328 | 386 | 772 | 21.45 | 42.9 | 0.094 | 0.047 | 0.113 | 0.0565
2 x 3 x 1 x 185 mm² | 2 | 3 | 1 | 185 | 1 x 185 mm² | 29.3 | 146.5 | 2560 | 15360 | 0.1 | 0.1275 | 0.063752 | 444 | 888 | 26.46 | 52.92 | 0.093 | 0.0465 | 0.112 | 0.056
2 x 3 x 1 x 240 mm² | 2 | 3 | 1 | 240 | 1 x 240 mm² | 32.5 | 162.5 | 3190 | 19140 | 0.0762 | 0.097159 | 0.048579 | 528 | 1056 | 34.32 | 68.64 | 0.09 | 0.045 | 0.108 | 0.054
2 x 3 x 1 x 300 mm² | 2 | 3 | 1 | 300 | 1 x 300 mm² | 35.2 | 176 | 3935 | 23610 | 0.0607 | 0.077395 | 0.038698 | 612 | 1224 | 42.9 | 85.8 | 0.089 | 0.0445 | 0.107 | 0.0535
2 x 3 x 1 x 400 mm² | 2 | 3 | 1 | 400 | 1 x 400 mm² | 0 | 0 | 0 | 0 | 0.047 | 0.059927 | 0.029964 | 0 | 0 | 42 | 84 | 0.086 | 0.043 | 0 | 0
3 x 3 x 1 x 240 mm² | 3 | 3 | 1 | 240 | 1 x 240 mm² | 32.5 | 260 | 3190 | 28710 | 0.0762 | 0.097159 | 0.032386 | 528 | 1584 | 34.32 | 102.96 | 0.09 | 0.03 | 0.108 | 0.036
3 x 3 x 1 x 300 mm² | 3 | 3 | 1 | 300 | 1 x 300 mm² | 35.2 | 281.6 | 3935 | 35415 | 0.0607 | 0.077395 | 0.025798 | 612 | 1836 | 42.9 | 128.7 | 0.089 | 0.029667 | 0.107 | 0.035667
3 x 3 x 1 x 400 mm² | 3 | 3 | 1 | 400 | 1 x 400 mm² | 0 | 0 | 0 | 0 | 0.047 | 0.059927 | 0.019976 | 0 | 0 | 42 | 126 | 0.086 | 0.028667 | 0 | 0
3 x 3 x 1 x 500 mm² | 3 | 3 | 1 | 500 | 1 x 500 mm² | 0 | 0 | 0 | 0 | 0.0366 | 0.046667 | 0.015556 | 0 | 0 | 70 | 210 | 0.085 | 0.028333 | 0 | 0
3 x 3 x 1 x 630 mm² | 3 | 3 | 1 | 630 | 1 x 630 mm² | 0 | 0 | 0 | 0 | 0.0283 | 0.036084 | 0.012028 | 0 | 0 | 88.2 | 264.6 | 0.036 | 0.012 | 0 | 0
4 x 3 x 1 x 240 mm² | 4 | 3 | 1 | 240 | 1 x 240 mm² | 32.5 | 357.5 | 3190 | 38280 | 0.0762 | 0.097159 | 0.02429 | 528 | 2112 | 34.32 | 137.28 | 0.09 | 0.0225 | 0.108 | 0.027
4 x 3 x 1 x 300 mm² | 4 | 3 | 1 | 300 | 1 x 300 mm² | 35.2 | 387.2 | 3935 | 47220 | 0.0607 | 0.077395 | 0.019349 | 612 | 2448 | 42.9 | 171.6 | 0.089 | 0.02225 | 0.107 | 0.02675
4 x 3 x 1 x 400 mm² | 4 | 3 | 1 | 400 | 1 x 400 mm² | 0 | 0 | 0 | 0 | 0.047 | 0.059927 | 0.014982 | 0 | 0 | 42 | 168 | 0.086 | 0.0215 | 0 | 0
4 x 3 x 1 x 500 mm² | 4 | 3 | 1 | 500 | 1 x 500 mm² | 0 | 0 | 0 | 0 | 0.0366 | 0.046667 | 0.011667 | 0 | 0 | 70 | 280 | 0.085 | 0.02125 | 0 | 0
4 x 3 x 1 x 630 mm² | 4 | 3 | 1 | 630 | 1 x 630 mm² | 0 | 0 | 0 | 0 | 0.0283 | 0.036084 | 0.009021 | 0 | 0 | 88.2 | 352.8 | 0.036 | 0.009 | 0 | 0
5 x 3 x 1 x 240 mm² | 5 | 3 | 1 | 240 | 1 x 240 mm² | 32.5 | 455 | 3190 | 47850 | 0.0762 | 0.097159 | 0.019432 | 528 | 2640 | 34.32 | 171.6 | 0.09 | 0.018 | 0.108 | 0.0216
5 x 3 x 1 x 300 mm² | 5 | 3 | 1 | 300 | 1 x 300 mm² | 35.2 | 492.8 | 3935 | 59025 | 0.0607 | 0.077395 | 0.015479 | 612 | 3060 | 42.9 | 214.5 | 0.089 | 0.0178 | 0.107 | 0.0214
5 x 3 x 1 x 400 mm² | 5 | 3 | 1 | 400 | 1 x 400 mm² | 0 | 0 | 0 | 0 | 0.047 | 0.059927 | 0.011985 | 0 | 0 | 42 | 210 | 0.086 | 0.0172 | 0 | 0
5 x 3 x 1 x 500 mm² | 5 | 3 | 1 | 500 | 1 x 500 mm² | 0 | 0 | 0 | 0 | 0.0366 | 0.046667 | 0.0093334 | 0 | 0 | 70 | 350 | 0.085 | 0.017 | 0 | 0
5 x 3 x 1 x 630 mm² | 5 | 3 | 1 | 630 | 1 x 630 mm² | 0 | 0 | 0 | 0 | 0.0283 | 0.036084 | 0.0072168 | 0 | 0 | 88.2 | 441 | 0.036 | 0.0072 | 0 | 0
6 x 3 x 1 x 240 mm² | 6 | 3 | 1 | 240 | 1 x 240 mm² | 32.5 | 552.5 | 3190 | 57420 | 0.0762 | 0.097159 | 0.016193 | 528 | 3168 | 34.32 | 205.92 | 0.09 | 0.015 | 0.108 | 0.018
6 x 3 x 1 x 300 mm² | 6 | 3 | 1 | 300 | 1 x 300 mm² | 35.2 | 598.4 | 3935 | 70830 | 0.0607 | 0.077395 | 0.012899 | 612 | 3672 | 42.9 | 257.4 | 0.089 | 0.014833 | 0.107 | 0.017833
6 x 3 x 1 x 400 mm² | 6 | 3 | 1 | 400 | 1 x 400 mm² | 0 | 0 | 0 | 0 | 0.047 | 0.059927 | 0.0099879 | 0 | 0 | 42 | 252 | 0.086 | 0.014333 | 0 | 0
6 x 3 x 1 x 500 mm² | 6 | 3 | 1 | 500 | 1 x 500 mm² | 0 | 0 | 0 | 0 | 0.0366 | 0.046667 | 0.0077778 | 0 | 0 | 70 | 420 | 0.085 | 0.014167 | 0 | 0
6 x 3 x 1 x 630 mm² | 6 | 3 | 1 | 630 | 1 x 630 mm² | 0 | 0 | 0 | 0 | 0.0283 | 0.036084 | 0.006014 | 0 | 0 | 88.2 | 529.2 | 0.036 | 0.006 | 0 | 0

## CABLE DATA PRYSMIAN
PRYSMIAN Cables according to NEK 606 III ed. 2004 & IEC 60092-300 (series)
TEOF RFOU
N° of cores x csa | Number of cores | Cross section core | Designation | Overall diameter approx. | Net weight approx. | D.C. resistance at 20 °C max. as per IEC 60228 | D.C. resistance at 90°C Correcting factor = (234,5+90)/254,5 | Current carrying capacities 45 °C free air | Fault current at 250 °C | Reactance** at 50 Hz | Reactance** at 60 Hz
n x mm2 |  | mm² |  | mm | kg/km | Ohm/km | Ohm/km | A | kA | Ohm/km | Ohm/km
1x10 | 1 | 10 | 1 x 10 mm² | 12.2 | 295 | 1.84 | 2.3461 | 70 | 1.43 | 0.129 | 0.154
1x16 | 1 | 16 | 1 x 16 mm² | 13.5 | 385 | 1.16 | 1.4791 | 93 | 2.29 | 0.12 | 0.145
1x25 | 1 | 25 | 1 x 25 mm² | 15.4 | 525 | 0.734 | 0.93589 | 117 | 3.58 | 0.113 | 0.136
1x35 | 1 | 35 | 1 x 35 mm² | 16.9 | 685 | 0.529 | 0.6745 | 147 | 5.01 | 0.111 | 0.133
1x50 | 1 | 50 | 1 x 50 mm² | 18.7 | 870 | 0.391 | 0.49854 | 180 | 7.15 | 0.107 | 0.129
1x70 | 1 | 70 | 1 x 70 mm² | 20.4 | 1105 | 0.27 | 0.34426 | 233 | 10.01 | 0.102 | 0.123
1x95 | 1 | 95 | 1 x 95 mm² | 22.8 | 1435 | 0.195 | 0.24863 | 285 | 13.59 | 0.099 | 0.118
1x120 | 1 | 120 | 1 x 120 mm² | 24.9 | 1745 | 0.154 | 0.19636 | 333 | 17.16 | 0.096 | 0.116
1x150 | 1 | 150 | 1 x 150 mm² | 26.8 | 2055 | 0.126 | 0.16066 | 386 | 21.45 | 0.094 | 0.113
1x185 | 1 | 185 | 1 x 185 mm² | 29.3 | 2560 | 0.1 | 0.1275 | 444 | 26.46 | 0.093 | 0.112
1x240 | 1 | 240 | 1 x 240 mm² | 32.5 | 3190 | 0.0762 | 0.097159 | 528 | 34.32 | 0.09 | 0.108
1x300 | 1 | 300 | 1 x 300 mm² | 35.2 | 3935 | 0.0607 | 0.077395 | 612 | 42.9 | 0.089 | 0.107
1x400 | 1 | 400 | 1 x 400 mm² |  |  | 0.047 | 0.059927 |  | 42 | 0.086
1x500 | 1 | 500 | 1 x 500 mm² |  |  | 0.0366 | 0.046667 |  | 70 | 0.085
1x630 | 1 | 630 | 1 x 630 mm² |  |  | 0.0283 | 0.036084 |  | 88.2 | 0.036
2x1,5 | 2 | 1,5 | 2 x 1,5 mm² | 13.6 | 295 | 12.2 | 15.5556 | 23 | 0.21 | 0.112 | 0.135
2x2,5 | 2 | 2,5 | 2 x 2,5 mm² | 14.4 | 335 | 7.56 | 9.6394 | 31 | 0.36 | 0.104 | 0.124
2x4 | 2 | 4 | 2 x 4 mm² | 16.1 | 445 | 4.7 | 5.9927 | 43 | 0.57 | 0.096 | 0.116
2x6 | 2 | 6 | 2 x 6 mm² | 17.1 | 520 | 3.11 | 3.9654 | 55 | 0.86 | 0.091 | 0.109
2x10 | 2 | 10 | 2 x 10 mm² | 19.3 | 680 | 1.84 | 2.3461 | 75 | 1.43 | 0.085 | 0.102
2x16 | 2 | 16 | 2 x 16 mm² | 21.7 | 955 | 1.16 | 1.4791 | 100 | 2.29 | 0.081 | 0.097
2x25 | 2 | 25 | 2 x 25 mm² | 25.9 | 1335 | 0.734 | 0.93589 | 130 | 3.58 | 0.08 | 0.096
2x35 | 2 | 35 | 2 x 35 mm² | 27.9 | 1595 | 0.529 | 0.6745 | 161 | 5.01 | 0.078 | 0.093
2x50 | 2 | 50 | 2 x 50 mm² | 31.9 | 2250 | 0.391 | 0.49854 | 196 | 7.15 | 0.077 | 0.093
3x1,5 | 3 | 1,5 | 3 x 1,5 mm² | 14.2 | 320 | 12.2 | 15.5556 | 20 | 0.21 | 0.112 | 0.135
3x2,5 | 3 | 2,5 | 3 x 2,5 mm² | 15.6 | 415 | 7.56 | 9.6394 | 28 | 0.36 | 0.104 | 0.124
3x4 | 3 | 4 | 3 x 4 mm² | 16.8 | 500 | 4.7 | 5.9927 | 37 | 0.57 | 0.096 | 0.116
3x6 | 3 | 6 | 3 x 6 mm² | 18.1 | 605 | 3.11 | 3.9654 | 47 | 0.86 | 0.091 | 0.109
3x10 | 3 | 10 | 3 x 10 mm² | 20.3 | 795 | 1.84 | 2.3461 | 65 | 1.43 | 0.085 | 0.102
3x16 | 3 | 16 | 3 x 16 mm² | 22.8 | 1125 | 1.16 | 1.4791 | 87 | 2.29 | 0.081 | 0.097
3x25 | 3 | 25 | 3 x 25 mm² | 27.5 | 1620 | 0.734 | 0.93589 | 110 | 3.58 | 0.08 | 0.096
3x35 | 3 | 35 | 3 x 35 mm² | 29.6 | 1955 | 0.529 | 0.6745 | 137 | 5.01 | 0.078 | 0.093
3x50 | 3 | 50 | 3 x 50 mm² | 33.9 | 2730 | 0.391 | 0.49854 | 167 | 7.15 | 0.077 | 0.093
3x70 | 3 | 70 | 3 x 70 mm² | 38.4 | 3655 | 0.27 | 0.34426 | 214 | 10.01 | 0.075 | 0.09
3x95 | 3 | 95 | 3 x 95 mm² | 43.8 | 4885 | 0.195 | 0.24863 | 259 | 13.59 | 0.074 | 0.089
3x120 | 3 | 120 | 3 x 120 mm² | 47.6 | 6000 | 0.154 | 0.19636 | 301 | 17.16 | 0.073 | 0.087
3x150 | 3 | 150 | 3 x 150 mm² | 52.4 | 7300 | 0.126 | 0.16066 | 347 | 21.45 | 0.073 | 0.087
3x185 | 3 | 185 | 3 x 185 mm² | 58.6 | 8960 | 0.1 | 0.1275 | 397 | 26.46 | 0.073 | 0.087
3x240 | 3 | 240 | 3 x 240 mm² | 66.1 | 11610 | 0.0762 | 0.097159 | 468 | 34.32 | 0.072 | 0.087
4x1,5 | 4 | 1,5 | 4 x 1,5 mm² | 15.7 | 350 | 12.2 | 15.5556 | 20 | 0.21 | 0.112 | 0.135
4x2,5 | 4 | 2,5 | 4 x 2,5 mm² | 16.6 | 425 | 7.56 | 9.6394 | 28 | 0.36 | 0.104 | 0.124
4x4 | 4 | 4 | 4 x 4 mm² | 18.1 | 590 | 4.7 | 5.9927 | 37 | 0.57 | 0.096 | 0.116
4x6 | 4 | 6 | 4 x 6 mm² | 9.5 | 725 | 3.11 | 3.9654 | 47 | 0.86 | 0.091 | 0.109
4x10 | 4 | 10 | 4 x 10 mm² | 22.1 | 955 | 1.84 | 2.3461 | 65 | 1.43 | 0.085 | 0.102
4x16 | 4 | 16 | 4 x 16 mm² | 25.2 | 1375 | 1.16 | 1.4791 | 87 | 2.29 | 0.081 | 0.097
4x25 | 4 | 25 | 4 x 25 mm² | 30 | 1965 | 0.734 | 0.93589 | 110 | 3.58 | 0.08 | 0.096
4x35 | 4 | 35 | 4 x 35 mm² | 32.4 | 2410 | 0.529 | 0.6745 | 137 | 5.01 | 0.078 | 0.093
4x50 | 4 | 50 | 4 x 50 mm² | 37.3 | 3365 | 0.391 | 0.49854 | 167 | 7.15 | 0.077 | 0.093
4x70 | 4 | 70 | 4 x 70 mm² | 42.1 | 4580 | 0.27 | 0.34426 | 214 | 10.01 | 0.075 | 0.09
4x95 | 4 | 95 | 4 x 95 mm² | 48.2 | 6020 | 0.195 | 0.24863 | 259 | 13.59 | 0.074 | 0.089
4x120 | 4 | 120 | 4 x 120 mm² | 52.7 | 7440 | 0.154 | 0.19636 | 301 | 17.16 | 0.073 | 0.087
5x1,5 | 5 | 1,5 | 5 x 1,5 mm² | 16.7 | 420 | 12.2 | 15.5556 | 12 | 0.21 | 0.112 | 0.135
7x1,5 | 7 | 1,5 | 7 x 1,5 mm² | 17.8 | 540 | 12.2 | 15.5556 | 11 | 0.21 | 0.112 | 0.135
12x1,5 | 12 | 1,5 | 12 x 1,5 mm² | 22.5 | 805 | 12.2 | 15.5556 | 9 | 0.21 | 0.112 | 0.135
19x1,5 | 19 | 1,5 | 19 x 1,5 mm² | 26 | 1100 | 12.2 | 15.5556 | 8 | 0.21 | 0.112 | 0.135
27x1,5 | 27 | 1,5 | 27 x 1,5 mm² | 30.6 | 1460 | 12.2 | 15.5556 | 7 | 0.21 | 0.112 | 0.135
37x1,5 | 37 | 1,5 | 37 x 1,5 mm² | 33.9 | 1840 | 12.2 | 15.5556 | 6 | 0.21 | 0.112 | 0.135
5x2,5 | 5 | 2,5 | 5 x 2,5 mm² | 18 | 555 | 7.56 | 9.6394 | 17 | 0.36 | 0.104 | 0.124
7x2,5 | 7 | 2,5 | 7 x 2,5 mm² | 19.2 | 655 | 7.56 | 9.6394 | 15 | 0.36 | 0.104 | 0.124
12x2,5 | 12 | 2,5 | 12 x 2,5 mm² | 24.5 | 995 | 7.56 | 9.6394 | 13 | 0.36 | 0.104 | 0.124
19x2,5 | 19 | 2,5 | 19 x 2,5 mm² | 28.2 | 1360 | 7.56 | 9.6394 | 11 | 0.36 | 0.104 | 0.124
27x2,5 | 27 | 2,5 | 27 x 2,5 mm² | 33.2 | 1815 | 7.56 | 9.6394 | 10 | 0.36 | 0.104 | 0.124
37x2,5 | 37 | 2,5 | 37 x 2,5 mm² | 37.1 | 2320 | 7.56 | 9.6394 | 9 | 0.36 | 0.104 | 0.124