## rev 02
No. | MONTH FR | LOCATION | AREA | PLANT/EQUIPMENT | QTY | M. TYPE | START DATE | FINISH DATE | RUNNING HOURS | MAINTENANCE JOB | DETAILED MAINTENANCE JOB | POS | DESCRIPTION | QTY | POS 2 | NAME | TIME
473 | 2014-01-01 | PLANT AREA and Others | Plant Area | Admin Building | 1 | PPM | 2014-01-01 | 2014-01-31 |  | Clean the Admin Building Floors periodically and keep the Building Clean always. | Clean the Admin Building Floors periodically and keep the Building Clean always.
474 | 2014-01-01 | PLANT AREA and Others | Garden | Garden | 1 | PPM | 2014-01-01 | 2014-01-31 |  | Pour water Continuously for the Plants and proper actions (daily basis). | Pour water Continuously for the Plants and proper actions (daily basis).
475 | 2014-01-01 | PLANT AREA and Others | Plant Area | Road, Land Scape & Admin Building | 1 | PPM | 2014-01-01 | 2014-01-31 |  | Cleaning of the complete plant area (weekly basis) | Cleaning of the complete plant area (weekly basis)
476 | 2014-01-01 | FST | RAS/SAS PS | RAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-01-02 | 2014-01-02 |  | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters. | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters.
477 | 2014-01-01 | FST | RAS/SAS PS | RAS/SAS Penstock Actuator | 1 | PPM | 2014-01-02 | 2014-01-02 |  | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
478 | 2014-01-01 | RLPS | RLPS PS | RLPS Pump 1,2 & 3 | 3 | PPM | 2014-01-02 | 2014-01-02 |  | Checking the condition of hoisting chains and cleaning the control panel. Checked the IR values and Resistance and Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. Checked the IR values and Resistance and Perform Run Test for the 3 pumps
479 | 2014-01-01 | AERATION | ATL 4 | ATL 4-Mix 2 | 4 | CM | 2014-01-03 | 2014-01-03 |  | repair of the mixer: replacement of the bearings, O-rings and mechanical seal. | repair of the mixer: replacement of the bearings
480 | 2014-01-01 | AERATION | ATL 4 | ATL 4-Mix 2 | 4 | CM | 2014-01-03 | 2014-01-03 |  | repair of the mixer: replacement of the bearings, O-rings and mechanical seal. | O-rings and mechanical seal.
481 | 2014-01-01 | INLET WORKS | GG Tank | Air lift pump 2 | 1 | CM | 2014-01-03 | 2014-01-03 |  | replacement of the pneumatic valve | replacement of the pneumatic valve
482 | 2014-01-01 | RLPS | RLPS PS | RLPS Pump 1 | 1 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the RLPS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Dismantle the RLPS Pump.No.1
483 | 2014-01-01 | RLPS | RLPS PS | RLPS Pump 1 | 1 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the RLPS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Replace the Bearings
484 | 2014-01-01 | RLPS | RLPS PS | RLPS Pump 1 | 1 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the RLPS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | O-rings
485 | 2014-01-01 | RLPS | RLPS PS | RLPS Pump 1 | 1 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the RLPS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Mechanical seal
486 | 2014-01-01 | RLPS | RLPS PS | RLPS Pump 1 | 1 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the RLPS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Re-assembling
487 | 2014-01-01 | RLPS | RLPS PS | RLPS Pump 1 | 1 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the RLPS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | painting with epoxy paint and Installation of the pump.
488 | 2014-01-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the SAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Dismantle the SAS Pump.No.1
489 | 2014-01-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the SAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Replace the Bearings
490 | 2014-01-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the SAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | O-rings
491 | 2014-01-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the SAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Mechanical seal
492 | 2014-01-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the SAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Re-assembling
493 | 2014-01-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | CM | 2014-01-03 | 2014-01-03 |  | Dismantle the SAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | painting with epoxy paint and Installation of the pump.
494 | 2014-01-01 | INLET WORKS | GG Tank | Grit Tank Penstock Actuator 1 & 2 | 1 | PPM | 2014-01-03 | 2014-01-03 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
495 | 2014-01-01 | INLET WORKS | Inlet | Inlet screen Penstock Acuator 1 & 2 | 1 | PPM | 2014-01-03 | 2014-01-03 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
496 | 2014-01-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-01-03 | 2014-01-03 |  | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser. | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser.
497 | 2014-01-01 | FST | RAS/SAS PS | RAS pumps 1 | 1 | CM | 2014-01-04 | 2014-01-04 |  | Dismantle the RAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Dismantle the RAS Pump.No.1
498 | 2014-01-01 | FST | RAS/SAS PS | RAS pumps 1 | 1 | CM | 2014-01-04 | 2014-01-04 |  | Dismantle the RAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Replace the Bearings
499 | 2014-01-01 | FST | RAS/SAS PS | RAS pumps 1 | 1 | CM | 2014-01-04 | 2014-01-04 |  | Dismantle the RAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | O-rings
500 | 2014-01-01 | FST | RAS/SAS PS | RAS pumps 1 | 1 | CM | 2014-01-04 | 2014-01-04 |  | Dismantle the RAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Mechanical seal
501 | 2014-01-01 | FST | RAS/SAS PS | RAS pumps 1 | 1 | CM | 2014-01-04 | 2014-01-04 |  | Dismantle the RAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | Re-assembling
502 | 2014-01-01 | FST | RAS/SAS PS | RAS pumps 1 | 1 | CM | 2014-01-04 | 2014-01-04 |  | Dismantle the RAS Pump.No.1, Replace the Bearings, O-rings, Mechanical seal, Re-assembling, painting with epoxy paint and Installation of the pump. | painting with epoxy paint and Installation of the pump.
503 | 2014-01-01 | INLET WORKS | Inlet | Grit Classifier | 1 | PPM | 2014-01-04 | 2014-01-04 |  | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container
504 | 2014-01-01 | FST | FST 4 | FST 4 | 4 | PM | 2014-01-07 | 2014-01-07 |  | Replacement of the Old scrapper Rubber with New one (top and bottom scrapper) | Replacement of the Old scrapper Rubber with New one (top and bottom scrapper)
505 | 2014-01-01 | FST | FST 1-4 | FST 1-4 | 4 | PPM | 2014-01-07 | 2014-01-07 |  | Clean the Chanel, Adjust the brushes. | Clean the Chanel, Adjust the brushes.
506 | 2014-01-01 | FST | FST Motors & Gear Boxes | FST Motors & Gear Boxes | 4 | PPM | 2014-01-07 | 2014-01-07 | wich clarif??? | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox
507 | 2014-01-01 | FST | FST | Level Sensors | 4 | PPM | 2014-01-07 | 2014-01-07 |  | Removed the DO Sensors , Completely Cleaned & Re-Installed. | Removed the DO Sensors , Completely Cleaned & Re-Installed.
508 | 2014-01-01 | INLET WORKS | Outfall PS | Outfall Pump 1 & 2 | 2 | PPM | 2014-01-07 | 2014-01-07 |  | Clean/Spray with pressurized water for the hoisting chains, Check the Megger and Resistance of the Pumps and Perform run test for the pumps | Clean/Spray with pressurized water for the hoisting chains, Check the Megger and Resistance of the Pumps and Perform run test for the pumps
509 | 2014-01-01 | FST | FST 1 | FST 1 | 4 | CM | 2014-01-08 | 2014-01-08 |  | Replacement of the damaged part of the Old Top scrapper Rubber with New one | Replacement of the damaged part of the Old Top scrapper Rubber with New one
510 | 2014-01-01 | AERATION | Blower Room | Aeration Blower B | 1 | PM | 2014-01-08 | 2014-01-08 | 18809.46 | Replacement of the blower oil with new one | Replacement of the blower oil with new one
511 | 2014-01-01 | AERATION | ATLs | Air Flow Meter | 12 | CM | 2014-01-10 | 2014-01-10 |  | Adjustement of the flowmeter setting. | Adjustement of the flowmeter setting.
512 | 2014-01-01 | AERATION | ATLs | Actuators | 12 | PM | 2014-01-10 | 2014-01-10 |  | Setting of the actuator for ATL 4-Zone 1 | Setting of the actuator for ATL 4-Zone 1
513 | 2014-01-01 | AERATION | ATLs | Actuators | 12 | PPM | 2014-01-10 | 2014-01-10 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
514 | 2014-01-01 | AERATION | ATLs | Air Flow Meter | 12 | PPM | 2014-01-10 | 2014-01-10 |  | Clean the Equipments completely & Check the Flow meter readings. | Clean the Equipments completely & Check the Flow meter readings.
515 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | Drain Belt 1 & 2 | 2 | PPM | 2014-01-10 | 2014-01-10 |  | Clean water spray nozzles and the filtrate through | Clean water spray nozzles and the filtrate through
516 | 2014-01-01 | LV/GEN SET | LV Panel | LV panel | 1 | PPM | 2014-01-10 | 2014-01-10 |  | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit
517 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | Manual Dosing Plant | 1 | PPM | 2014-01-10 | 2014-01-10 |  | Clean the Polymer Mixer and Mixing Tank Completely | Clean the Polymer Mixer and Mixing Tank Completely
518 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | Polymer Dosing Plant | 1 | PPM | 2014-01-10 | 2014-01-10 |  | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water
519 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | Thick Sludge Pumps | 2 | PPM | 2014-01-10 | 2014-01-10 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
520 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | Thin Sludge Pumps | 2 | PPM | 2014-01-10 | 2014-01-10 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
521 | 2014-01-01 | FST | FST 2 | Bell Mouth Actuators | 4 | PPM | 2014-01-11 | 2014-01-11 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
522 | 2014-01-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filter Effluent water Valve 1-5 | 5 | PPM | 2014-01-11 | 2014-01-11 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
523 | 2014-01-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Air Valve 1-5 | 5 | PPM | 2014-01-11 | 2014-01-11 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
524 | 2014-01-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash water Valve 1-5 | 5 | PPM | 2014-01-11 | 2014-01-11 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
525 | 2014-01-01 | AERATION | Blower Room | Aeration Blower C & D | 2 | PPM | 2014-01-12 | 2014-01-12 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
526 | 2014-01-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Valve 1-5 | 5 | PPM | 2014-01-12 | 2014-01-12 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
527 | 2014-01-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Influent Valve 1-5 | 5 | PPM | 2014-01-12 | 2014-01-12 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
528 | 2014-01-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Influent Valve 1-5 | 5 | PPM | 2014-01-12 | 2014-01-12 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
529 | 2014-01-01 | INLET WORKS | G1 Pumping Station | pH Meter in G1 Line | 1 | PM | 2014-01-14 | 2014-01-14 |  | Clean the Electrode scale deposits, Organic oil or Grease. Remove the Sensor unit from the pit and perform calibration | Clean the Electrode scale deposits
530 | 2014-01-01 | TERTIARY EQUIPMENTS | Out Fall Valve (to the sea) | TE. Pumping station | 1 | PM | 2014-01-14 | 2014-01-14 |  | Setting of the actuator Limit settings. | Setting of the actuator Limit settings.
531 | 2014-01-01 | TERTIARY EQUIPMENTS | Out Fall Valve (to the sea) | TE. Pumping station | 1 | PPM | 2014-01-14 | 2014-01-14 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
532 | 2014-01-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1, 2 & 3 | 3 | PPM | 2014-01-14 | 2014-01-14 |  | cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
533 | 2014-01-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1, 2 & 3 | 3 | PPM | 2014-01-14 | 2014-01-14 |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
534 | 2014-01-01 | AERATION | ATL 2 | ATL 2-Mix 1-4 | 4 | PPM | 2014-01-15 | 2014-01-15 |  | Checking the running Amp. Wash the Hoist Chains. | Checking the running Amp. Wash the Hoist Chains.
535 | 2014-01-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blower 2 | 1 | PPM | 2014-01-16 | 2014-01-16 |  | Adjustment / Re-Tightening of the blower V-Belt | Adjustment / Re-Tightening of the blower V-Belt
536 | 2014-01-01 | INLET WORKS | GG Tank | Grease Scraper 1 & 2 | 2 | PM | 2014-01-17 | 2014-01-17 |  | Replacement of the teflon paddles | Replacement of the teflon paddles
537 | 2014-01-01 | AERATION | ATL 1 - 4 | MLSS Sensor | 4 | PPM | 2014-01-17 | 2014-01-17 |  | Removed the MLSS Sensors , Completely Cleaned & Re-Installed. | Removed the MLSS Sensors , Completely Cleaned & Re-Installed.
538 | 2014-01-01 | AERATION | ATL 3 | ATL 3-Mix 1-4 | 4 | PPM | 2014-01-18 | 2014-01-18 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
539 | 2014-01-01 | AERATION | ATL 4 | ATL 4-Mix 1-4 | 4 | PPM | 2014-01-18 | 2014-01-18 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
540 | 2014-01-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blower 1 | 1 | PPM | 2014-01-18 | 2014-01-18 |  | Adjustment / Re-Tightening of the blower V-Belt | Adjustment / Re-Tightening of the blower V-Belt
541 | 2014-01-01 | INLET WORKS | Inlet | Fine Screen 1 & 2 | 2 | PPM | 2014-01-20 | 2014-01-20 |  | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes
542 | 2014-01-01 | AERATION | LCP panel | Aeration Blower B | 1 | CM | 2014-01-21 | 2014-01-21 |  | Replacement of the damaged Emergency Cut Off Relay from the LCP panel &Fix New one. | Replacement of the damaged Emergency Cut Off Relay from the LCP panel &Fix New one.
543 | 2014-01-01 | AERATION | Blower Room | Aeration blowers A, B, C & D | 4 | PPM | 2014-01-21 | 2014-01-21 |  | Checking the terminals of all LCP panels for the HV blowers | Checking the terminals of all LCP panels for the HV blowers
544 | 2014-01-01 | INLET WORKS | GG Tank | Grease Scraper 1 & 2 | 2 | PPM | 2014-01-22 | 2014-01-22 |  | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails. | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails.
545 | 2014-01-01 | TOXIC HOLDING TANK | Sludge Holding Tank | Submersible Aerator 1 | 1 | PPM | 2014-01-22 | 2014-01-22 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator
546 | 2014-01-01 | TOXIC HOLDING TANK | Toxic Holding Tank | Submersible Aerator 1 & 2 | 2 | PPM | 2014-01-22 | 2014-01-22 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator
547 | 2014-01-01 | WASH WATER ROOM | Wash Water Room | Chlorine analyser | 1 | PPM | 2014-01-24 | 2014-01-24 |  | Cleaning of the Chlorine analyser in wash water pump room | Cleaning of the Chlorine analyser in wash water pump room
548 | 2014-01-01 | AERATION | ATL 1 | ATL 1-Mix 1-4 | 4 | PPM | 2014-01-25 | 2014-01-25 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
549 | 2014-01-01 | INLET WORKS | GG Tank | Air lift pump 1 & 2 | 2 | PPM | 2014-01-25 | 2014-01-25 |  | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves. | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves.
550 | 2014-01-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | FAT Aerators 1 & 2 | 2 | PPM | 2014-01-25 | 2014-01-25 |  | Checking of oil level and oil condition. Perform Run test and Check the Running Amps. | Checking of oil level and oil condition. Perform Run test and Check the Running Amps.
551 | 2014-01-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Fixed Aerator 1 & 2 | 2 | PPM | 2014-01-25 | 2014-01-25 |  | Hose down turbine deflection shield, floats and structural beams. Apply Grease | Hose down turbine deflection shield, floats and structural beams. Apply Grease
552 | 2014-01-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Floating Aerator 2 & 3 | 2 | PPM | 2014-01-25 | 2014-01-25 |  | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound. | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound.
553 | 2014-01-01 | AERATION | ATLs | IRP | 3 | PPM | 2014-01-25 | 2014-01-25 |  | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains
554 | 2014-01-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Sludge Transfer Pumps | 2 | PPM | 2014-01-25 | 2014-01-25 |  | Checking and cleaning of the lifting chains. checking NRV. | Checking and cleaning of the lifting chains. checking NRV.
555 | 2014-01-01 | AERATION | Blower Room | Aeration Blower B | 1 | CM | 2014-01-26 | 2014-01-26 |  | Dismantling of the Blower B Motor. Replace the motor Bearings with New ones. Cleaning of the stator and removal of the accumulated old grease. Re-Assemble and reinstallation of the blower motor. Coupling of the motor to the blower and running of the blower. | Dismantling of the Blower B Motor.
556 | 2014-01-01 | AERATION | Blower Room | Aeration Blower B | 1 | CM | 2014-01-26 | 2014-01-26 |  | Dismantling of the Blower B Motor. Replace the motor Bearings with New ones. Cleaning of the stator and removal of the accumulated old grease. Re-Assemble and reinstallation of the blower motor. Coupling of the motor to the blower and running of the blower. | Replace the motor Bearings with New ones.
557 | 2014-01-01 | AERATION | Blower Room | Aeration Blower B | 1 | CM | 2014-01-26 | 2014-01-26 |  | Dismantling of the Blower B Motor. Replace the motor Bearings with New ones. Cleaning of the stator and removal of the accumulated old grease. Re-Assemble and reinstallation of the blower motor. Coupling of the motor to the blower and running of the blower. | Cleaning of the stator and removal of the accumulated old grease.
558 | 2014-01-01 | AERATION | Blower Room | Aeration Blower B | 1 | CM | 2014-01-26 | 2014-01-26 |  | Dismantling of the Blower B Motor. Replace the motor Bearings with New ones. Cleaning of the stator and removal of the accumulated old grease. Re-Assemble and reinstallation of the blower motor. Coupling of the motor to the blower and running of the blower. | Re-Assemble and reinstallation of the blower motor.
559 | 2014-01-01 | AERATION | Blower Room | Aeration Blower B | 1 | CM | 2014-01-26 | 2014-01-26 |  | Dismantling of the Blower B Motor. Replace the motor Bearings with New ones. Cleaning of the stator and removal of the accumulated old grease. Re-Assemble and reinstallation of the blower motor. Coupling of the motor to the blower and running of the blower. | Coupling of the motor to the blower and running of the blower.
560 | 2014-01-01 | AERATION | MCC 3 | MCC 3 | 1 | CM | 2014-01-26 | 2014-01-26 |  | Perform Industrial Wiring works for the New AC, connexion and running of the AC. | Perform Industrial Wiring works for the New AC
561 | 2014-01-01 | AERATION | MCC 3 | MCC 3 | 1 | CM | 2014-01-26 | 2014-01-26 |  | Perform Industrial Wiring works for the New AC, connexion and running of the AC. | connexion and running of the AC.
562 | 2014-01-01 | LV/GEN SET | LV Panel | Gen-set | 1 | PPM | 2014-01-26 | 2014-01-26 |  | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant. | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant.
563 | 2014-01-01 | AERATION | Blower Room | Aeration Blower A & B | 2 | PPM | 2014-01-26 | 2014-01-26 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
564 | 2014-01-01 | INLET WORKS | MCC 2 | MCC 2 | 1 | PPM | 2014-01-26 | 2014-01-26 |  | Cleaning of the MCC panel, Checking of the terminals connections. | Cleaning of the MCC panel, Checking of the terminals connections.
565 | 2014-01-01 | AERATION | MCC 3 | MCC 3 | 1 | PPM | 2014-01-26 | 2014-01-26 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
566 | 2014-01-01 | WASH WATER ROOM | Wash Water Room | Wash water room | 1 | PPM | 2014-01-26 | 2014-01-26 |  | Cleaning of electrical panel Clean the Wash water room | Cleaning of electrical panel Clean the Wash water room
567 | 2014-01-01 | SLUDGE DIGESTER | MCC 5 | MCC 5 | 1 | CM | 2014-01-27 | 2014-01-27 |  | Perform Industrial Wiring works for the New AC, connexion and running of the AC. | Perform Industrial Wiring works for the New AC
568 | 2014-01-01 | SLUDGE DIGESTER | MCC 5 | MCC 5 | 1 | CM | 2014-01-27 | 2014-01-27 |  | Perform Industrial Wiring works for the New AC, connexion and running of the AC. | connexion and running of the AC.
569 | 2014-01-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | PPM | 2014-01-27 | 2014-01-27 |  | Clean Completely and Check the devices | Clean Completely and Check the devices
570 | 2014-01-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-01-27 | 2014-01-27 |  | Cleaning the chlorine room, booster pumps and checking safety device for chlorine gas leaks. | Cleaning the chlorine room, booster pumps and checking safety device for chlorine gas leaks.
571 | 2014-01-01 | INLET WORKS | GG Tank | GG Blower 1, 2 & 3 | 3 | PPM | 2014-01-27 | 2014-01-27 |  | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves. | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves.
572 | 2014-01-01 | FST | MCC 4 | MCC 4 | 1 | PPM | 2014-01-27 | 2014-01-27 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
573 | 2014-01-01 | SLUDGE DIGESTER | MCC 5 | MCC 5 | 1 | PPM | 2014-01-27 | 2014-01-27 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit
574 | 2014-01-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PM | 2014-01-28 | 2014-01-28 |  | Cleaning of the blowers and blowers room Cleaning of the air filter, checking the motor cooling fan condition and retighten the control panel terminal. Replacement of the gear oil. | Cleaning of the blowers and blowers room
575 | 2014-01-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PM | 2014-01-28 | 2014-01-28 |  | Cleaning of the blowers and blowers room Cleaning of the air filter, checking the motor cooling fan condition and retighten the control panel terminal. Replacement of the gear oil. | Cleaning of the air filter
576 | 2014-01-01 | SLUDGE DIGESTER | Aerobic sludge digester | Decanter valve | 1 | PPM | 2014-01-28 | 2014-01-28 |  | Hose down decanter unit | Hose down decanter unit
577 | 2014-01-01 | TERTIARY EQUIPMENTS | MCC 6 | MCC 6 | 1 | PPM | 2014-01-28 | 2014-01-28 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps
578 | 2014-01-01 | STORM WATER PS | STORM WATER PS | MCC 8 | 1 | PPM | 2014-01-29 | 2014-01-29 |  | Checking the temperature of the bus bar and cleaning the control panel | Checking the temperature of the bus bar and cleaning the control panel
579 | 2014-01-01 | STORM WATER PS | Storm Water Pumps | Storm Water Pump 1, 2, & 3 | 3 | PPM | 2014-01-29 | 2014-01-29 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps
580 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | MCC 7 | 1 | CM | 2014-01-30 | 2014-01-30 |  | Perform Industrial Wiring works for the New AC, connexion and running of the AC. | Perform Industrial Wiring works for the New AC
581 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | MCC 7 | 1 | CM | 2014-01-30 | 2014-01-30 |  | Perform Industrial Wiring works for the New AC, connexion and running of the AC. | connexion and running of the AC.
582 | 2014-01-01 | MCC 7 | Sludge Thickening Plant | MCC 7 | 1 | PPM | 2014-01-30 | 2014-01-30 |  | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals
583 | 2014-01-01 | TERTIARY EQUIPMENTS | Tertiary Filter | Back Wash Pumps 1 & 2 | 2 | PPM | 2014-01-31 | 2014-01-31 |  | cleaning/ spray with pressurized water the hoisting chains and wash water pumps. And checking the condition of hoisting chains. | cleaning/ spray with pressurized water the hoisting chains and wash water pumps. And checking the condition of hoisting chains.
584 | 2014-02-01 | PLANT AREA and Others | Plant Area | Admin Building | 1 | PPM | 2014-02-01 | 2014-02-28 |  | Clean the Admin Building Floors periodically and keep the Building Clean always. | Clean the Admin Building Floors periodically and keep the Building Clean always.
585 | 2014-02-01 | PLANT AREA and Others | Garden | Garden | 1 | PPM | 2014-02-01 | 2014-02-28 |  | Pour water Continuously for the Plants and proper actions (daily basis). | Pour water Continuously for the Plants and proper actions (daily basis).
586 | 2014-02-01 | PLANT AREA and Others | Plant Area | Road, Land Scape & Admin Building | 1 | PPM | 2014-02-01 | 2014-02-28 |  | Cleaning of the complete plant area (weekly basis) | Cleaning of the complete plant area (weekly basis)
587 | 2014-02-01 | INLET WORKS | Inlet | Grit Classifier | 1 | PM | 2014-02-02 | 2014-02-02 |  | Emptying and cleaning the grit container, replacement of the damaged oil seal. | Emptying and cleaning the grit container
588 | 2014-02-01 | INLET WORKS | GG Tank | GG Blower 1, 2 & 3 | 3 | PM | 2014-02-04 | 2014-02-04 |  | Replacement of the old oil. | Replacement of the old oil.
589 | 2014-02-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filter Effluent water Valve 1-5 | 5 | PPM | 2014-02-04 | 2014-02-04 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
590 | 2014-02-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Air Valve 1-5 | 5 | PPM | 2014-02-04 | 2014-02-04 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
591 | 2014-02-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Valve 1-5 | 5 | PPM | 2014-02-04 | 2014-02-04 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
592 | 2014-02-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash water Valve 1-5 | 5 | PPM | 2014-02-04 | 2014-02-04 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
593 | 2014-02-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Influent Valve 1-5 | 5 | PPM | 2014-02-04 | 2014-02-04 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
594 | 2014-02-01 | AERATION | ATL 1 | ATL 1-Mix 1-4 | 4 | PPM | 2014-02-06 | 2014-02-06 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
595 | 2014-02-01 | AERATION | ATL 2 | ATL 2-Mix 1-4 | 4 | PPM | 2014-02-06 | 2014-02-06 |  | Checking the running Amp. Wash the Hoist Chains. | Checking the running Amp. Wash the Hoist Chains.
596 | 2014-02-01 | AERATION | ATL 3 | ATL 3-Mix 1-4 | 4 | PPM | 2014-02-06 | 2014-02-06 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
597 | 2014-02-01 | AERATION | ATL 4 | ATL 4-Mix 1-4 | 4 | PPM | 2014-02-06 | 2014-02-06 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
598 | 2014-02-01 | AERATION | ATLs | IRP | 3 | PPM | 2014-02-06 | 2014-02-06 |  | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains
599 | 2014-02-01 | INLET WORKS | Outfall PS | Outfall Pump 1 & 2 | 2 | PPM | 2014-02-06 | 2014-02-06 |  | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps
600 | 2014-02-01 | PLANT AREA and Others | Main Entrance | NS-STP Main Gate | 1 | CM | 2014-02-07 | 2014-02-07 |  | Repair the Main Gate Sliding Door, Replace the Sensors, Relays and Adjust the Gear of the Motor, now working Good. | Repair the Main Gate Sliding Door
601 | 2014-02-01 | PLANT AREA and Others | Main Entrance | NS-STP Main Gate | 1 | CM | 2014-02-07 | 2014-02-07 |  | Repair the Main Gate Sliding Door, Replace the Sensors, Relays and Adjust the Gear of the Motor, now working Good. | Replace the Sensors
602 | 2014-02-01 | PLANT AREA and Others | Main Entrance | NS-STP Main Gate | 1 | CM | 2014-02-07 | 2014-02-07 |  | Repair the Main Gate Sliding Door, Replace the Sensors, Relays and Adjust the Gear of the Motor, now working Good. | Relays and Adjust the Gear of the Motor
603 | 2014-02-01 | PLANT AREA and Others | Main Entrance | NS-STP Main Gate | 1 | CM | 2014-02-07 | 2014-02-07 |  | Repair the Main Gate Sliding Door, Replace the Sensors, Relays and Adjust the Gear of the Motor, now working Good. | now working Good.
604 | 2014-02-01 | AERATION | ATLs | Actuators | 12 | PPM | 2014-02-07 | 2014-02-07 |  | Cleaning the actuator motor and body, Exercising of the actuator manually. | Cleaning the actuator motor and body, Exercising of the actuator manually.
605 | 2014-02-01 | AERATION | ATLs | Air Flow Meter | 12 | PPM | 2014-02-07 | 2014-02-07 |  | Clean the Equipments completely & Check the Flow meter readings. | Clean the Equipments completely & Check the Flow meter readings.
606 | 2014-02-01 | AERATION | ATL 4 | ATL 4-Mix 2 | 1 | CM | 2014-02-08 | 2014-02-08 |  | Repair of the damaged mixer; replacement of the mechanical seal, bearings and O rings. | Repair of the damaged mixer; replacement of the mechanical seal
607 | 2014-02-01 | AERATION | ATL 4 | ATL 4-Mix 2 | 1 | CM | 2014-02-08 | 2014-02-08 |  | Repair of the damaged mixer; replacement of the mechanical seal, bearings and O rings. | bearings and O rings.
608 | 2014-02-01 | FST | FST 2 | Bell Mouth Actuators | 4 | PPM | 2014-02-11 | 2014-02-11 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
609 | 2014-02-01 | PLANT AREA and Others | Security Cabin | NS-STP Security Cabin - Water Tank | 1 | CM | 2014-02-12 | 2014-02-12 |  | Repair the Float switch of the Water Tank and Now the Pump is working Good. | Repair the Float switch of the Water Tank and Now the Pump is working Good.
610 | 2014-02-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | CM | 2014-02-12 | 2014-02-12 |  | Fix NC contactor and give the connections. | Fix NC contactor and give the connections.
611 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | Thick Sludge Pumps | 2 | PM | 2014-02-12 | 2014-02-12 |  | Clean the outer body of the Pump, Apply Primer and Paint the exterior of the Pumps completely. | Clean the outer body of the Pump
612 | 2014-02-01 | AERATION | Blower Room | Aeration Blower C & D | 2 | PPM | 2014-02-12 | 2014-02-12 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
613 | 2014-02-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PPM | 2014-02-12 | 2014-02-12 |  | Check the condition and tightness of the Blower V-Belts. | Check the condition and tightness of the Blower V-Belts.
614 | 2014-02-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers Air Flow Actuator | 1 | PPM | 2014-02-12 | 2014-02-12 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
615 | 2014-02-01 | FST | FST 1-4 | FST 1-4 | 4 | PPM | 2014-02-13 | 2014-02-13 |  | Clean the Chanel, Adjust the brushes. | Clean the Chanel, Adjust the brushes.
616 | 2014-02-01 | FST | RAS/SAS PS | RAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-02-13 | 2014-02-13 |  | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters. | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters.
617 | 2014-02-01 | FST | RAS/SAS PS | RAS/SAS Penstock Actuator | 1 | PPM | 2014-02-13 | 2014-02-13 |  | Lubricating the thread bar, Cleaning the actuator motor and body, Exercising of the actuator manually. | Lubricating the thread bar, Cleaning the actuator motor and body, Exercising of the actuator manually.
618 | 2014-02-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-02-13 | 2014-02-13 |  | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser. | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser.
619 | 2014-02-01 | TERTIARY EQUIPMENTS | Out Fall Valve (to the sea) | TE. Pumping station | 1 | PPM | 2014-02-13 | 2014-02-13 |  | Cleaning the out body for actuator, Checking the grease condition. | Cleaning the out body for actuator, Checking the grease condition.
620 | 2014-02-01 | FST | FST 4 | Motor & Gear Box | 1 | PPM | 2014-02-15 | 2014-02-15 |  | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox
621 | 2014-02-01 | FST | FST | Level Sensors | 4 | PPM | 2014-02-15 | 2014-02-15 |  | Removed the DO Sensors , Completely Cleaned & Re-Installed. | Removed the DO Sensors , Completely Cleaned & Re-Installed.
622 | 2014-02-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filter 4, Valve 4 | 1 | CM | 2014-02-16 | 2014-02-16 |  | Remove the damaged Isolator Switch and replace it with New one. | Remove the damaged Isolator Switch and replace it with New one.
623 | 2014-02-01 | TOXIC HOLDING TANK | Sludge Holding Tank | Submersible Aerator 1 | 1 | PPM | 2014-02-17 | 2014-02-17 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator
624 | 2014-02-01 | TOXIC HOLDING TANK | Toxic Holding Tank | Submersible Aerator 1 & 2 | 2 | PPM | 2014-02-17 | 2014-02-17 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator
625 | 2014-02-01 | SLUDGE DIGESTER | Aerobic sludge digester | Decanter valve | 1 | PPM | 2014-02-18 | 2014-02-18 |  | Hose down decanter unit | Hose down decanter unit
626 | 2014-02-01 | LV/GEN SET | LV Panel | Gen-set | 1 | PPM | 2014-02-18 | 2014-02-18 |  | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant. | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant.
627 | 2014-02-01 | WASH WATER ROOM | Wash Water Room | Chlorine analyser | 1 | PPM | 2014-02-19 | 2014-02-19 |  | Cleaning of the Chlorine analyser in wash water pump room | Cleaning of the Chlorine analyser in wash water pump room
628 | 2014-02-01 | STORM WATER PS | STORM WATER PS | MCC 8 | 1 | PPM | 2014-02-19 | 2014-02-19 |  | Checking the temperature of the bus bar and cleaning the control panel | Checking the temperature of the bus bar and cleaning the control panel
629 | 2014-02-01 | STORM WATER PS | Storm Water Pumps | Storm Water Pump 1, 2, & 3 | 3 | PPM | 2014-02-19 | 2014-02-19 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps
630 | 2014-02-01 | WASH WATER ROOM | Wash Water Room | wash water Pumps | 3 | PPM | 2014-02-19 | 2014-02-19 |  | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp. | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp.
631 | 2014-02-01 | WASH WATER ROOM | Wash Water Room | Wash water room | 1 | PPM | 2014-02-19 | 2014-02-19 |  | Cleaning of electrical panel Clean the Wash water room | Cleaning of electrical panel Clean the Wash water room
632 | 2014-02-01 | AERATION | Blower Room | Aeration blowers A, B, C & D | 4 | PPM | 2014-02-20 | 2014-02-20 |  | Checking the terminals of all LCP panels for the HV blowers | Checking the terminals of all LCP panels for the HV blowers
633 | 2014-02-01 | RLPS | RLPS PS | RLPS Pump 1,2 & 3 | 3 | PPM | 2014-02-20 | 2014-02-20 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps
634 | 2014-02-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PPM | 2014-02-20 | 2014-02-20 |  | Cleaning of the blowers and blowers room Cleaning of the air filter, Check the gear oil. | Cleaning of the blowers and blowers room Cleaning of the air filter, Check the gear oil.
635 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | Drain Belt 1 & 2 | 2 | PPM | 2014-02-21 | 2014-02-21 |  | Clean water spray nozzles and the filtrate through | Clean water spray nozzles and the filtrate through
636 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | Manual Dosing Plant | 1 | PPM | 2014-02-21 | 2014-02-21 |  | Clean the Polymer Mixer and Mixing Tank Completely | Clean the Polymer Mixer and Mixing Tank Completely
637 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | MCC 7 | 1 | PPM | 2014-02-21 | 2014-02-21 |  | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals
638 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | MCC 7 | 1 | PPM | 2014-02-21 | 2014-02-21 |  | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals
639 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | Polymer Dosing Plant | 1 | PPM | 2014-02-21 | 2014-02-21 |  | Clean the Mixing Tank. Clean the entire plant Floor with wash water | Clean the Mixing Tank. Clean the entire plant Floor with wash water
640 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | Thick Sludge Pumps | 2 | PPM | 2014-02-21 | 2014-02-21 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
641 | 2014-02-01 | MCC 7 | Sludge Thickening Plant | Thin Sludge Pumps | 2 | PPM | 2014-02-21 | 2014-02-21 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
642 | 2014-02-01 | FST | RAS/SAS PS | RAS pumps 4 | 1 | PM | 2014-02-23 | 2014-02-23 |  | Checking of the pump condition, painting and replacement of the damaged holder with new stainless steel holder. | Checking of the pump condition
643 | 2014-02-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | FAT Aerators 1 & 2 | 2 | PPM | 2014-02-23 | 2014-02-23 |  | Checking of oil level and oil condition. Perform Run test and Check the Running Amps. | Checking of oil level and oil condition. Perform Run test and Check the Running Amps.
644 | 2014-02-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Fixed Aerator 1 & 2 | 2 | PPM | 2014-02-23 | 2014-02-23 |  | Hose down turbine deflection shield, floats and structural beams. Apply Grease | Hose down turbine deflection shield, floats and structural beams. Apply Grease
645 | 2014-02-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Floating Aerator 2 & 3 | 2 | PPM | 2014-02-23 | 2014-02-23 |  | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound. | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound.
646 | 2014-02-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Sludge Transfer Pumps | 2 | PPM | 2014-02-23 | 2014-02-23 |  | Checking and cleaning of the lifting chains. checking NRV. | Checking and cleaning of the lifting chains. checking NRV.
647 | 2014-02-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | CM | 2014-02-24 | 2014-02-24 |  | Pump under maintenance; it presented abnormal sound. | Pump under maintenance; it presented abnormal sound.
648 | 2014-02-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | CM | 2014-02-24 | 2014-02-24 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Paint the Pump completely by Epoxy paint. | Lift up the Pump
649 | 2014-02-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | CM | 2014-02-24 | 2014-02-24 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Paint the Pump completely by Epoxy paint. | Replace the old Bearings and Installed New Ones
650 | 2014-02-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | CM | 2014-02-24 | 2014-02-24 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Paint the Pump completely by Epoxy paint. | replace the Old Mechanical Seal
651 | 2014-02-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | CM | 2014-02-24 | 2014-02-24 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Paint the Pump completely by Epoxy paint. | O-rings and Re-Assemble the pump. Paint the Pump completely by Epoxy paint.
652 | 2014-02-01 | INLET WORKS | Inlet | Fine Screen 1 & 2 | 2 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes
653 | 2014-02-01 | INLET WORKS | GG Tank | Grit Tank Penstock Actuator 1 & 2 | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning the actuator motor and body, Exercising of the actuator manually. | Cleaning the actuator motor and body, Exercising of the actuator manually.
654 | 2014-02-01 | AERATION | Blower Room | Aeration Blower A & B | 2 | PPM | 2014-02-25 | 2014-02-25 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
655 | 2014-02-01 | INLET WORKS | Inlet | Inlet screen Penstock Acuator 1 & 2 | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning the actuator motor and body, Exercising of the actuator manually. | Cleaning the actuator motor and body, Exercising of the actuator manually.
656 | 2014-02-01 | LV/GEN SET | LV Panel | LV panel | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit
657 | 2014-02-01 | TERTIARY EQUIPMENTS | MCC 6 | MCC 6 | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps
658 | 2014-02-01 | INLET WORKS | MCC 2 | MCC 2 | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning of the MCC panel, Checking of the terminals connections. | Cleaning of the MCC panel, Checking of the terminals connections.
659 | 2014-02-01 | AERATION | MCC 3 | MCC 3 | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
660 | 2014-02-01 | FST | MCC 4 | MCC 4 | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
661 | 2014-02-01 | SLUDGE DIGESTER | MCC 5 | MCC 5 | 1 | PPM | 2014-02-25 | 2014-02-25 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit
662 | 2014-02-01 | INLET WORKS | GG Tank | GG Blower 1 | 1 | CM | 2014-02-26 | 2014-02-26 |  | Replace the Damaged Emergency/Selector switch unit, Fix the New One. | Replace the Damaged Emergency/Selector switch unit
663 | 2014-02-01 | INLET WORKS | GG Tank | GG Blower 1 | 1 | CM | 2014-02-26 | 2014-02-26 |  | Replace the Damaged Emergency/Selector switch unit, Fix the New One. | Fix the New One.
664 | 2014-02-01 | INLET WORKS | GG Tank | Air Compressor | 1 | PPM | 2014-02-26 | 2014-02-26 |  | Clean the air filter, Clean the Compressor Unit | Clean the air filter, Clean the Compressor Unit
665 | 2014-02-01 | INLET WORKS | GG Tank | Air lift pump 1 & 2 | 2 | PPM | 2014-02-26 | 2014-02-26 |  | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves. | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves.
666 | 2014-02-01 | INLET WORKS | GG Tank | GG Blower 1, 2 & 3 | 3 | PPM | 2014-02-26 | 2014-02-26 |  | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves. | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves.
667 | 2014-02-01 | INLET WORKS | GG Tank | Grease Scraper 1 & 2 | 2 | PPM | 2014-02-26 | 2014-02-26 |  | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails. | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails.
668 | 2014-02-01 | INLET WORKS | Inlet | Grit Classifier | 2 | PPM | 2014-02-26 | 2014-02-26 |  | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container
669 | 2014-02-01 | AERATION | ATL 1 - 4 | MLSS Sensor | 4 | PPM | 2014-02-26 | 2014-02-26 |  | Removed the MLSS Sensors , Completely Cleaned & Re-Installed. | Removed the MLSS Sensors , Completely Cleaned & Re-Installed.
670 | 2014-02-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | PPM | 2014-02-27 | 2014-02-27 |  | Clean Completely and Check the devices | Clean Completely and Check the devices
671 | 2014-02-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-02-27 | 2014-02-27 |  | Cleaning the chlorine room, booster pumps and checking safety device for chlorine gas leaks. | Cleaning the chlorine room, booster pumps and checking safety device for chlorine gas leaks.
672 | 2014-03-01 | PLANT AREA and Others | Plant Area | Admin Building | 1 | PPM | 2014-03-01 | 2014-03-31 |  | Clean the Admin Building Floors periodically and keep the Building Clean always. | Clean the Admin Building Floors periodically and keep the Building Clean always.
673 | 2014-03-01 | PLANT AREA and Others | Garden | Garden | 1 | PPM | 2014-03-01 | 2014-03-31 |  | Pour water Continuously for the Plants and proper actions (daily basis). | Pour water Continuously for the Plants and proper actions (daily basis).
674 | 2014-03-01 | PLANT AREA and Others | Garden | Garden | 1 | PPM | 2014-03-01 | 2014-03-31 |  | Pour water Continuously for the Plants and proper actions (daily basis). | Pour water Continuously for the Plants and proper actions (daily basis).
675 | 2014-03-01 | LV/GEN SET | LV Panel | LV panel | 1 | PPM | 2014-03-01 | 2014-03-01 |  | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit
676 | 2014-03-01 | INLET WORKS | MCC 2 | MCC 2 | 1 | PPM | 2014-03-01 | 2014-03-01 |  | Cleaning of the MCC panel, Checking of the terminals connections. | Cleaning of the MCC panel, Checking of the terminals connections.
677 | 2014-03-01 | PLANT AREA and Others | Plant Area | Road, Land Scape & Admin Building | 1 | PPM | 2014-03-01 | 2014-03-31 |  | Cleaning of the complete plant area (weekly basis) | Cleaning of the complete plant area (weekly basis)
678 | 2014-03-01 | FST | MCC 4 | MCC 4 | 1 | PPM | 2014-03-03 | 2014-03-03 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
679 | 2014-03-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PPM | 2014-03-03 | 2014-03-03 |  | Cleaning of the blowers and blowers room. Cleaning of the air filter, Check the gear oil. Check the condition and tightness of the Blower V-Belts. Clean the screens, Clean the blower unit. | Cleaning of the blowers and blowers room. Cleaning of the air filter, Check the gear oil. Check the condition and tightness of the Blower V-Belts. Clean the screens, Clean the blower unit.
680 | 2014-03-01 | SLUDGE DIGESTER | MCC 5 | MCC 5 | 1 | PPM | 2014-03-04 | 2014-03-04 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit
681 | 2014-03-01 | TERTIARY EQUIPMENTS | MCC 6 | MCC 6 | 1 | PPM | 2014-03-05 | 2014-03-05 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps
682 | 2014-03-01 | AERATION | ATLs | Actuators | 12 | PPM | 2014-03-07 | 2014-03-07 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
683 | 2014-03-01 | FST | FST 1-4 | Bell Mouth Actuators | 4 | PPM | 2014-03-07 | 2014-03-07 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
684 | 2014-03-01 | FST | FST 2 | Bell Mouth Actuators | 1 | PPM | 2014-03-07 | 2014-03-07 |  | Cleaning the out body for actuator, Checking the grease condition, Re-Set the Limit settings. | Cleaning the out body for actuator, Checking the grease condition, Re-Set the Limit settings.
685 | 2014-03-01 | INLET WORKS | GG Tank | Grit Tank Penstock Actuator 1 & 2 | 1 | PPM | 2014-03-07 | 2014-03-07 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
686 | 2014-03-01 | INLET WORKS | Inlet | Inlet screen Penstock Acuator 1 & 2 | 1 | PPM | 2014-03-07 | 2014-03-07 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
687 | 2014-03-01 | INLET WORKS | GG Tank | Air Compressor | 1 | PPM | 2014-03-08 | 2014-03-08 |  | Clean the air filter, Clean the Compressor Unit | Clean the air filter, Clean the Compressor Unit
688 | 2014-03-01 | INLET WORKS | GG Tank | Air lift pump 1 & 2 | 2 | PPM | 2014-03-08 | 2014-03-08 |  | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves. | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves.
689 | 2014-03-01 | INLET WORKS | Inlet | Fine Screen 1 & 2 | 2 | PPM | 2014-03-08 | 2014-03-08 |  | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes
690 | 2014-03-01 | INLET WORKS | GG Tank | GG Blower 1, 2 & 3 | 3 | PPM | 2014-03-08 | 2014-03-08 |  | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves. | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves.
691 | 2014-03-01 | INLET WORKS | GG Tank | Grease Scraper 1 & 2 | 2 | PPM | 2014-03-08 | 2014-03-08 |  | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails. | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails.
692 | 2014-03-01 | INLET WORKS | Inlet | Grit Classifier | 1 | PPM | 2014-03-08 | 2014-03-08 |  | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container
693 | 2014-03-01 | AERATION | ATL 1 | ATL 1-Mix 1-4 | 4 | PPM | 2014-03-10 | 2014-03-10 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
694 | 2014-03-01 | AERATION | ATL 2 | ATL 2-Mix 1-4 | 4 | PPM | 2014-03-10 | 2014-03-10 |  | Checking the running Amp. Wash the Hoist Chains. | Checking the running Amp. Wash the Hoist Chains.
695 | 2014-03-01 | AERATION | ATL 3 | ATL 3-Mix 1-4 | 4 | PPM | 2014-03-10 | 2014-03-10 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
696 | 2014-03-01 | AERATION | ATL 4 | ATL 4-Mix 1-4 | 4 | PPM | 2014-03-10 | 2014-03-10 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
697 | 2014-03-01 | LV/GEN SET | LV Panel | Gen-set | 1 | PPM | 2014-03-10 | 2014-03-10 |  | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant. | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant.
698 | 2014-03-01 | WASH WATER ROOM | Wash Water Room | Chlorine analyser | 1 | PPM | 2014-03-11 | 2014-03-11 |  | Cleaning of the Chlorine analyser in wash water pump room | Cleaning of the Chlorine analyser in wash water pump room
699 | 2014-03-01 | MCC 7 | Sludge Thickening Plant | Drain Belt 1 & 2 | 2 | PPM | 2014-03-11 | 2014-03-11 |  | Clean water spray nozzles and the filtrate through | Clean water spray nozzles and the filtrate through
700 | 2014-03-01 | MCC 7 | Sludge Thickening Plant | Manual Dosing Plant | 1 | PPM | 2014-03-11 | 2014-03-11 |  | Clean the Polymer Mixer and Mixing Tank Completely | Clean the Polymer Mixer and Mixing Tank Completely
701 | 2014-03-01 | MCC 7 | Sludge Thickening Plant | Polymer Dosing Plant | 1 | PPM | 2014-03-11 | 2014-03-11 |  | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water
702 | 2014-03-01 | MCC 7 | Sludge Thickening Plant | Thick Sludge Pumps | 2 | PPM | 2014-03-11 | 2014-03-11 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
703 | 2014-03-01 | MCC 7 | Sludge Thickening Plant | Thin Sludge Pumps | 2 | PPM | 2014-03-11 | 2014-03-11 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
704 | 2014-03-01 | WASH WATER ROOM | Wash Water Room | Wash water Panel | 1 | PPM | 2014-03-11 | 2014-03-11 |  | Cleaning of the panel, Check the tightness of the terminal connection and check the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the panel, Check the tightness of the terminal connection and check the A/C unit Replacement of the fused Panel Indication Lamps
705 | 2014-03-01 | WASH WATER ROOM | Wash Water Room | wash water Pumps | 3 | PPM | 2014-03-11 | 2014-03-11 |  | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp. | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp.
706 | 2014-03-01 | WASH WATER ROOM | Wash Water Room | Wash water room | 1 | PPM | 2014-03-11 | 2014-03-11 |  | Cleaning of electrical panel Clean the Wash water room | Cleaning of electrical panel Clean the Wash water room
707 | 2014-03-01 | AERATION | ATLs | DO Sensors | 12 | PPM | 2014-03-13 | 2014-03-13 |  | Remove / Lift up the Sensor unit and clean completely the unit and lower down. | Remove / Lift up the Sensor unit and clean completely the unit and lower down.
708 | 2014-03-01 | AERATION | ATL 1 - 4 | MLSS Sensor | 4 | PPM | 2014-03-13 | 2014-03-13 |  | Removed the MLSS Sensors , Completely Cleaned & Re-Installed. | Removed the MLSS Sensors , Completely Cleaned & Re-Installed.
709 | 2014-03-01 | FST | FST | Level Sensors | 4 | PPM | 2014-03-14 | 2014-03-14 |  | Removed the DO Sensors , Completely Cleaned & Re-Installed. | Removed the DO Sensors , Completely Cleaned & Re-Installed.
710 | 2014-03-01 | FST | RAS/SAS PS | RAS/SAS Penstock Actuator | 1 | PPM | 2014-03-14 | 2014-03-14 |  | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
711 | 2014-03-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Floating Aerator 2 | 1 | PM | 2014-03-15 | 2014-03-15 |  | Remove the Motor from the Unit, Dismantle the Motor, Replace the Old Damaged Bearings, Clean the stator completely, Re-Assemble the Motor and Fix back to the base. Check the Running Condition. Working Good | Remove the Motor from the Unit
712 | 2014-03-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | PPM | 2014-03-17 | 2014-03-17 |  | Clean Completely and Check the devices | Clean Completely and Check the devices
713 | 2014-03-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-03-17 | 2014-03-17 |  | Cleaning the chlorine room, Check the booster pumps. | Cleaning the chlorine room, Check the booster pumps.
714 | 2014-03-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-03-17 | 2014-03-17 |  | Clean the Chlorine room, Check the Safety device for Chlorine gas leaks. | Clean the Chlorine room, Check the Safety device for Chlorine gas leaks.
715 | 2014-03-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filter Effluent water Valve 1-5 | 5 | PPM | 2014-03-17 | 2014-03-17 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
716 | 2014-03-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Air Valve 1-5 | 5 | PPM | 2014-03-17 | 2014-03-17 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
717 | 2014-03-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Valve 1-5 | 5 | PPM | 2014-03-17 | 2014-03-17 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
718 | 2014-03-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash water Valve 1-5 | 5 | PPM | 2014-03-17 | 2014-03-17 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
719 | 2014-03-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Influent Valve 1-5 | 5 | PPM | 2014-03-17 | 2014-03-17 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
720 | 2014-03-01 | TERTIARY EQUIPMENTS | Tertiary Filter | Back Wash Pumps 1 & 2 | 3 | PPM | 2014-03-18 | 2014-03-18 |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
721 | 2014-03-01 | STORM WATER PS | STORM WATER PS | MCC 8 | 1 | PPM | 2014-03-19 | 2014-03-19 |  | Checking the temperature of the bus bar and cleaning the control panel | Checking the temperature of the bus bar and cleaning the control panel
722 | 2014-03-01 | STORM WATER PS | Storm Water Pumps | Storm Water Pump 1, 2, & 3 | 3 | PPM | 2014-03-19 | 2014-03-19 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps
723 | 2014-03-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Fixed Aerator 1 & 2 | 2 | PPM | 2014-03-20 | 2014-03-20 |  | Hose down turbine deflection shield, floats and structural beams. | Hose down turbine deflection shield, floats and structural beams.
724 | 2014-03-01 | AERATION | Blower Room | Aeration Blower A & B | 2 | PPM | 2014-03-21 | 2014-03-21 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
725 | 2014-03-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1, 2 & 3 | 3 | PPM | 2014-03-21 | 2014-03-21 |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
726 | 2014-03-01 | FST | RAS/SAS PS | RAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-03-22 | 2014-03-22 |  | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters. | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters.
727 | 2014-03-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-03-22 | 2014-03-22 |  | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser. | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser.
728 | 2014-03-01 | SLUDGE DIGESTER | Aerobic sludge digester | Decanter valve | 1 | PPM | 2014-03-23 | 2014-03-23 |  | Hose down decanter unit | Hose down decanter unit
729 | 2014-03-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | FAT Aerators 1 & 2 | 2 | PPM | 2014-03-23 | 2014-03-23 |  | Checking of oil level and oil condition. Perform Run test and Check the Running Amps. | Checking of oil level and oil condition. Perform Run test and Check the Running Amps.
730 | 2014-03-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Sludge Transfer Pumps | 2 | PPM | 2014-03-23 | 2014-03-23 |  | Checking and cleaning of the lifting chains. checking NRV. | Checking and cleaning of the lifting chains. checking NRV.
731 | 2014-03-01 | TOXIC HOLDING TANK | Toxic Holding Tank | Submersible Aerator 1 & 2 | 2 | PPM | 2014-03-23 | 2014-03-23 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator
732 | 2014-03-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | CM | 2014-03-25 | 2014-03-25 |  | Replace the damaged Selector switch of the booster pump in the panel and fix new. | Replace the damaged Selector switch of the booster pump in the panel and fix new.
733 | 2014-03-01 | AERATION | ATLs | ATL 3-Mix 1-3-4 | 16 | PPM | 2014-03-25 | 2014-03-25 |  | Clean the Complete Junction Boxes and check the tightness condition of the wires inside the JBs. | Clean the Complete Junction Boxes and check the tightness condition of the wires inside the JBs.
734 | 2014-03-01 | AERATION | Blower Room | Aeration Blower C & D | 2 | PPM | 2014-03-25 | 2014-03-25 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
735 | 2014-03-01 | AERATION | Blower Room | Aeration blowers A, B, C & D | 4 | PPM | 2014-03-25 | 2014-03-25 |  | Checking the terminals of all LCP panels for the HV blowers | Checking the terminals of all LCP panels for the HV blowers
736 | 2014-03-01 | AERATION | MCC 3 | MCC 3 | 1 | PPM | 2014-03-25 | 2014-03-25 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
737 | 2014-03-01 | RLPS | RLPS PS | RLPS Pump 1,2 & 3 | 3 | PPM | 2014-03-25 | 2014-03-25 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps
738 | 2014-03-01 | AERATION | ATL 4 | Air Flow Meter | 1 | PM | 2014-03-28 | 2014-03-28 |  | Clean the Equipment Completely, Adjust the settings of the Flowmeter. | Clean the Equipment Completely
739 | 2014-03-01 | AERATION | ATLs | Air Flow Meter | 12 | PPM | 2014-03-28 | 2014-03-28 |  | Clean the Equipments completely & Check the Flow meter readings. | Clean the Equipments completely & Check the Flow meter readings.
740 | 2014-03-01 | AERATION | ATLs | IRP | 3 | PPM | 2014-03-28 | 2014-03-28 |  | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains
741 | 2014-03-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Floating Aerator 2 & 3 | 2 | PPM | 2014-03-29 | 2014-03-29 |  | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound. | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound.
742 | 2014-03-01 | FST | FST 1-4 | FST 1-4 | 4 | PPM | 2014-03-29 | 2014-03-29 |  | Clean the Chanel, Adjust the brushes. | Clean the Chanel, Adjust the brushes.
743 | 2014-03-01 | FST | FST Motors & Gear Boxes | FST Motors & Gear Boxes | 4 | PPM | 2014-03-29 | 2014-03-29 |  | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox
744 | 2014-03-01 | INLET WORKS | Outfall PS | Outfall Pump 1 & 2 | 2 | PPM | 2014-03-30 | 2014-03-30 |  | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps
745 | 2014-03-01 | TOXIC HOLDING TANK | Sludge Holding Tank | Submersible Aerator 1 | 1 | PPM | 2014-03-31 | 2014-03-31 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator
746 | 2014-04-01 | PLANT AREA and Others | Plant Area | Admin Building | 1 | PPM | 2014-04-01 | 2014-04-30 |  | Clean the Admin Building Floors periodically and keep the Building Clean always. | Clean the Admin Building Floors periodically and keep the Building Clean always.
747 | 2014-04-01 | PLANT AREA and Others | Garden | Garden | 1 | PPM | 2014-04-01 | 2014-04-30 |  | Pour water Continuously for the Plants and proper actions (daily basis). | Pour water Continuously for the Plants and proper actions (daily basis).
748 | 2014-04-01 | LV/GEN SET | LV Panel | Gen-set | 1 | PPM | 2014-04-01 | 2014-04-01 |  | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant. Check the Batteries. Check the Fuel Level | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant. Check the Batteries. Check the Fuel Level
749 | 2014-04-01 | LV/GEN SET | LV Panel | LV panel | 1 | PPM | 2014-04-01 | 2014-04-01 |  | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit
750 | 2014-04-01 | PLANT AREA and Others | Plant Area | Road, Land Scape & Admin Building | 1 | PPM | 2014-04-01 | 2014-04-30 |  | Cleaning of the complete plant area (weekly basis) | Cleaning of the complete plant area (weekly basis)
751 | 2014-04-01 | INLET WORKS | GG Tank | Grit Tank Penstock Actuator 1 & 2 | 1 | PPM | 2014-04-02 | 2014-04-02 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
752 | 2014-04-01 | INLET WORKS | Inlet | Inlet screen Penstock Acuator 1 & 2 | 1 | PPM | 2014-04-02 | 2014-04-02 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
753 | 2014-04-01 | AERATION | ATLs | IRP | 3 | PPM | 2014-04-03 | 2014-04-03 |  | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains
754 | 2014-04-01 | INLET WORKS | MCC 2 | MCC 2 | 1 | PPM | 2014-04-03 | 2014-04-03 |  | Cleaning of the MCC panel, Checking of the terminals connections. | Cleaning of the MCC panel, Checking of the terminals connections.
755 | 2014-04-01 | AERATION | ATL 1 | DO Sensors | 3 | CM | 2014-04-04 | 2014-04-04 |  | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good
756 | 2014-04-01 | AERATION | ATL 2 | DO Sensors | 3 | CM | 2014-04-05 | 2014-04-05 |  | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good
757 | 2014-04-01 | AERATION | ATL 3 | DO Sensors | 3 | CM | 2014-04-06 | 2014-04-06 |  | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good
758 | 2014-04-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Floating Aerator 2 | 1 | PM | 2014-04-06 | 2014-04-06 |  | Dismantle the Cable of the FLA-2 and Check the Insulation, cut the damaged Part and Check the Insulation, Found Good, Re-Fix the Cable for the FLA-2, running Good. | Dismantle the Cable of the FLA-2 and Check the Insulation
759 | 2014-04-01 | AERATION | ATL 4 | DO Sensors | 3 | CM | 2014-04-07 | 2014-04-07 |  | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good | Remove / Lift up the Old Sensor unit and clean completely the unit and replace Sensor Module by New Ones. Calibrate the DO sensors and Check the readings with Portable DO Meter. Working good
760 | 2014-04-01 | WASH WATER ROOM | Wash Water Room | Wash water room | 1 | CM | 2014-04-07 | 2014-04-07 |  | Replace the Old repaired VFD and Fix back the New VFD. Adjust the settings and Now running Good. | Replace the Old repaired VFD and Fix back the New VFD. Adjust the settings and Now running Good.
761 | 2014-04-01 | TERTIARY EQUIPMENTS | Tertiary Filter | Back Wash Pumps 1 & 2 | 3 | PPM | 2014-04-07 | 2014-04-07 |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
762 | 2014-04-01 | WASH WATER ROOM | Wash Water Room | Chlorine analyser | 1 | PPM | 2014-04-07 | 2014-04-07 |  | Cleaning of the Chlorine analyser in wash water pump room | Cleaning of the Chlorine analyser in wash water pump room
763 | 2014-04-01 | AERATION | MCC 3 | MCC 3 | 1 | PPM | 2014-04-07 | 2014-04-07 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
764 | 2014-04-01 | WASH WATER ROOM | Wash Water Room | Wash water Panel | 1 | PPM | 2014-04-07 | 2014-04-07 |  | Cleaning of the panel, Check the tightness of the terminal connection and check the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the panel, Check the tightness of the terminal connection and check the A/C unit Replacement of the fused Panel Indication Lamps
765 | 2014-04-01 | WASH WATER ROOM | Wash Water Room | wash water Pumps | 3 | PPM | 2014-04-07 | 2014-04-07 |  | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp. | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp.
766 | 2014-04-01 | WASH WATER ROOM | Wash Water Room | Wash water room | 1 | PPM | 2014-04-07 | 2014-04-07 |  | Cleaning of electrical panel Clean the Wash water room | Cleaning of electrical panel Clean the Wash water room
767 | 2014-04-01 | AERATION | ATL 1 - 4 | MLSS Sensor | 4 | PPM | 2014-04-08 | 2014-04-08 |  | Removed the MLSS Sensors , Completely Cleaned & Re-Installed. | Removed the MLSS Sensors , Completely Cleaned & Re-Installed.
768 | 2014-04-01 | AERATION | Blower Room | Aeration Blower A & B | 2 | PPM | 2014-04-10 | 2014-04-10 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
769 | 2014-04-01 | AERATION | ATLs | ATL 1-Mix 1-4 | 16 | PPM | 2014-04-11 | 2014-04-11 |  | Clean the Complete Junction Boxes and check the tightness condition of the wires inside the JBs. | Clean the Complete Junction Boxes and check the tightness condition of the wires inside the JBs.
770 | 2014-04-01 | AERATION | ATL 1 | ATL 2-Mix 1-4 | 4 | PPM | 2014-04-11 | 2014-04-11 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
771 | 2014-04-01 | AERATION | ATL 2 | ATL 3-Mix 1-4 | 4 | PPM | 2014-04-11 | 2014-04-11 |  | Checking the running Amp. Wash the Hoist Chains. | Checking the running Amp. Wash the Hoist Chains.
772 | 2014-04-01 | AERATION | ATL 3 | ATL 4-Mix 1-4 | 4 | PPM | 2014-04-11 | 2014-04-11 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
773 | 2014-04-01 | AERATION | ATL 4 | ATL 2-Mix 2-3-4 | 4 | PPM | 2014-04-11 | 2014-04-11 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
774 | 2014-04-01 | SLUDGE DIGESTER | Aerobic sludge digester | Decanter valve | 1 | PPM | 2014-04-12 | 2014-04-12 |  | Hose down decanter unit , Clean the Unit | Hose down decanter unit , Clean the Unit
775 | 2014-04-01 | FST | RAS/SAS PS | RAS Pumps 1 | 1 | CM | 2014-04-13 | 2014-04-13 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Fix New Lifting Hook. Paint the Pump completely by Epoxy paint. | Lift up the Pump
776 | 2014-04-01 | FST | RAS/SAS PS | RAS Pumps 1 | 1 | CM | 2014-04-13 | 2014-04-13 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Fix New Lifting Hook. Paint the Pump completely by Epoxy paint. | Replace the old Bearings and Installed New Ones
777 | 2014-04-01 | FST | RAS/SAS PS | RAS Pumps 1 | 1 | CM | 2014-04-13 | 2014-04-13 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Fix New Lifting Hook. Paint the Pump completely by Epoxy paint. | replace the Old Mechanical Seal
778 | 2014-04-01 | FST | RAS/SAS PS | RAS Pumps 1 | 1 | CM | 2014-04-13 | 2014-04-13 |  | Lift up the Pump, Replace the old Bearings and Installed New Ones, replace the Old Mechanical Seal, O-rings and Re-Assemble the pump. Fix New Lifting Hook. Paint the Pump completely by Epoxy paint. | O-rings and Re-Assemble the pump. Fix New Lifting Hook. Paint the Pump completely by Epoxy paint.
779 | 2014-04-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PPM | 2014-04-13 | 2014-04-13 |  | Cleaning of the blowers and blowers room. Cleaning of the air filter, Check the gear oil. Check the condition and tightness of the Blower V-Belts. Clean the screens, Clean the blower unit. | Cleaning of the blowers and blowers room. Cleaning of the air filter, Check the gear oil. Check the condition and tightness of the Blower V-Belts. Clean the screens, Clean the blower unit.
780 | 2014-04-01 | AERATION | ATLs | Air Flow Meter | 12 | PPM | 2014-04-14 | 2014-04-14 |  | Clean the Equipments completely & Check the Flow meter readings. | Clean the Equipments completely & Check the Flow meter readings.
781 | 2014-04-01 | INLET WORKS | GG Tank | Air Compressor | 1 | PPM | 2014-04-15 | 2014-04-15 |  | Clean the air filter, Clean the Compressor Unit | Clean the air filter, Clean the Compressor Unit
782 | 2014-04-01 | INLET WORKS | GG Tank | Air lift pump 1 & 2 | 2 | PPM | 2014-04-15 | 2014-04-15 |  | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves. | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves.
783 | 2014-04-01 | AERATION | Blower Room | Aeration blowers A, B, C & D | 4 | PPM | 2014-04-15 | 2014-04-15 |  | Checking the terminals of all LCP panels for the HV blowers | Checking the terminals of all LCP panels for the HV blowers
784 | 2014-04-01 | AERATION | ATLs | Actuators | 12 | PPM | 2014-04-16 | 2014-04-16 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
785 | 2014-04-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filter Effluent water Valve 1-5 | 5 | PPM | 2014-04-16 | 2014-04-16 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
786 | 2014-04-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Air Valve 1-5 | 5 | PPM | 2014-04-16 | 2014-04-16 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
787 | 2014-04-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Valve 1-5 | 5 | PPM | 2014-04-16 | 2014-04-16 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
788 | 2014-04-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash water Valve 1-5 | 5 | PPM | 2014-04-16 | 2014-04-16 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
789 | 2014-04-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Influent Valve 1-5 | 5 | PPM | 2014-04-16 | 2014-04-16 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
790 | 2014-04-01 | INLET WORKS | GG Tank | Grease Scraper 1 & 2 | 2 | PPM | 2014-04-17 | 2014-04-17 |  | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails. | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails.
791 | 2014-04-01 | TOXIC HOLDING TANK | Sludge Holding Tank | Submersible Aerator 1 | 1 | PPM | 2014-04-17 | 2014-04-17 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator
792 | 2014-04-01 | TOXIC HOLDING TANK | Toxic Holding Tank | Submersible Aerator 1 & 2 | 2 | PPM | 2014-04-17 | 2014-04-17 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator
793 | 2014-04-01 | FST | FST 1-4 | FST 1-4 | 4 | PPM | 2014-04-19 | 2014-04-19 |  | Clean the Chanel, Adjust the brushes. | Clean the Chanel, Adjust the brushes.
794 | 2014-04-01 | FST | FST Motors & Gear Boxes | FST Motors & Gear Boxes | 4 | PPM | 2014-04-19 | 2014-04-19 |  | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox
795 | 2014-04-01 | INLET WORKS | Inlet | Fine Screen 1 & 2 | 2 | PPM | 2014-04-20 | 2014-04-20 |  | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes
796 | 2014-04-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-04-21 | 2014-04-21 |  | Cleaning the chlorine room, Check the booster pumps. | Cleaning the chlorine room, Check the booster pumps.
797 | 2014-04-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-04-21 | 2014-04-21 |  | Clean the Chlorine room, Check the Safety device for Chlorine gas leaks. | Clean the Chlorine room, Check the Safety device for Chlorine gas leaks.
798 | 2014-04-01 | TERTIARY EQUIPMENTS | MCC 6 | MCC 6 | 1 | PPM | 2014-04-21 | 2014-04-21 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps
799 | 2014-04-01 | INLET WORKS | Inlet | Grit Classifier | 1 | PPM | 2014-04-22 | 2014-04-22 |  | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container
800 | 2014-04-01 | INLET WORKS | GG Tank | GG Blower 1, 2 & 3 | 3 | PPM | 2014-04-24 | 2014-04-24 |  | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves. | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves.
801 | 2014-04-01 | AERATION | Blower Room | Aeration Blower C & D | 2 | PPM | 2014-04-24 | 2014-04-24 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
802 | 2014-04-01 | SLUDGE DIGESTER | MCC 5 | MCC 5 | 1 | PPM | 2014-04-24 | 2014-04-24 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit
803 | 2014-04-01 | RLPS | RLPS PS | RLPS Pump 1,2 & 3 | 3 | PPM | 2014-04-24 | 2014-04-24 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps
804 | 2014-04-01 | STORM WATER PS | STORM WATER PS | MCC 8 | 1 | PPM | 2014-04-26 | 2014-04-26 |  | Checking the temperature of the bus bar and cleaning the control panel | Checking the temperature of the bus bar and cleaning the control panel
805 | 2014-04-01 | FST | RAS/SAS PS | RAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-04-26 | 2014-04-26 |  | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters. | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters.
806 | 2014-04-01 | FST | RAS/SAS PS | RAS/SAS Penstock Actuator | 1 | PPM | 2014-04-26 | 2014-04-26 |  | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
807 | 2014-04-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-04-26 | 2014-04-26 |  | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser. | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser.
808 | 2014-04-01 | STORM WATER PS | Storm Water Pumps | Storm Water Pump 1, 2, & 3 | 3 | PPM | 2014-04-26 | 2014-04-26 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps
809 | 2014-04-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | FAT Aerators 1 & 2 | 2 | PPM | 2014-04-27 | 2014-04-27 |  | Checking of oil level and oil condition. Perform Run test and Check the Running Amps. | Checking of oil level and oil condition. Perform Run test and Check the Running Amps.
810 | 2014-04-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Fixed Aerator 1 & 2 | 2 | PPM | 2014-04-27 | 2014-04-27 |  | Hose down turbine deflection shield, floats and structural beams. | Hose down turbine deflection shield, floats and structural beams.
811 | 2014-04-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Floating Aerator 2 & 3 | 2 | PPM | 2014-04-27 | 2014-04-27 |  | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound. | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound.
812 | 2014-04-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Sludge Transfer Pumps | 2 | PPM | 2014-04-27 | 2014-04-27 |  | Checking and cleaning of the lifting chains. checking NRV. | Checking and cleaning of the lifting chains. checking NRV.
813 | 2014-04-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1, 2 & 3 | 3 | PPM | 2014-04-27 | 2014-04-27 |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
814 | 2014-04-01 | FST | FST | Level Sensors | 4 | PPM | 2014-04-28 | 2014-04-28 |  | Removed the DO Sensors , Completely Cleaned & Re-Installed. | Removed the DO Sensors , Completely Cleaned & Re-Installed.
815 | 2014-04-01 | FST | MCC 4 | MCC 4 | 1 | PPM | 2014-04-28 | 2014-04-28 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
816 | 2014-04-01 | MCC 7 | Sludge Thickening Plant | Drain Belt 1 & 2 | 2 | PPM | 2014-04-29 | 2014-04-29 |  | Clean water spray nozzles and the filtrate through | Clean water spray nozzles and the filtrate through
817 | 2014-04-01 | FST | FST 1-4 | Bell Mouth Actuators | 4 | PPM | 2014-04-29 | 2014-04-29 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
818 | 2014-04-01 | MCC 7 | Sludge Thickening Plant | Manual Dosing Plant | 1 | PPM | 2014-04-29 | 2014-04-29 |  | Clean the Polymer Mixer and Mixing Tank Completely | Clean the Polymer Mixer and Mixing Tank Completely
819 | 2014-04-01 | MCC 7 | Sludge Thickening Plant | MCC 7 | 1 | PPM | 2014-04-29 | 2014-04-29 |  | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals
820 | 2014-04-01 | INLET WORKS | Outfall PS | Outfall Pump 1 & 2 | 2 | PPM | 2014-04-29 | 2014-04-29 |  | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps
821 | 2014-04-01 | MCC 7 | Sludge Thickening Plant | Polymer Dosing Plant | 1 | PPM | 2014-04-29 | 2014-04-29 |  | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water
822 | 2014-04-01 | MCC 7 | Sludge Thickening Plant | Thick Sludge Pumps | 2 | PPM | 2014-04-29 | 2014-04-29 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
823 | 2014-04-01 | MCC 7 | Sludge Thickening Plant | Thin Sludge Pumps | 2 | PPM | 2014-04-29 | 2014-04-29 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
824 | 2014-04-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | CM | 2014-04-30 | 2014-04-30 |  | Replace the damaged Selector switch of the booster pump in the panel and fix new. | Replace the damaged Selector switch of the booster pump in the panel and fix new.
825 | 2014-04-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | PPM | 2014-04-30 | 2014-04-30 |  | Clean Completely and Check the devices | Clean Completely and Check the devices
826 | 2014-05-01 | PLANT AREA and Others | Plant Area | Admin Building | 1 | PPM | 2014-05-01 | 2014-05-31 |  | Clean the Admin Building Floors periodically and keep the Building Clean always. | Clean the Admin Building Floors periodically and keep the Building Clean always.
827 | 2014-05-01 | PLANT AREA and Others | Plant Area | Road, Land Scape & Admin Building | 1 | PPM | 2014-05-01 | 2014-05-31 |  | Cleaning of the complete plant area (weekly basis) | Cleaning of the complete plant area (weekly basis)
828 | 2014-05-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | PM | 2014-05-02 | 2014-05-02 |  | the pump presents abnormal vibration; Lift up the Pump for repair | the pump presents abnormal vibration;
829 | 2014-05-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | PM | 2014-05-02 | 2014-05-02 |  | the pump presents abnormal vibration; Lift up the Pump for repair | Lift up the Pump for repair
830 | 2014-05-01 | INLET WORKS | Inlet | Fine Screen 1 & 2 | 2 | PPM | 2014-05-02 | 2014-05-02 |  | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes
831 | 2014-05-01 | INLET WORKS | GG Tank | Grease Scraper 1 & 2 | 2 | PPM | 2014-05-03 | 2014-05-03 |  | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails. | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails.
832 | 2014-05-01 | INLET WORKS | Inlet | Grit Classifier | 1 | PPM | 2014-05-03 | 2014-05-03 |  | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container
833 | 2014-05-01 | FST | MCC 4 | MCC 4 | 1 | PPM | 2014-05-03 | 2014-05-03 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
834 | 2014-05-01 | FST | RAS/SAS PS | RAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-05-03 | 2014-05-03 |  | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters. | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters.
835 | 2014-05-01 | FST | RAS/SAS PS | RAS/SAS Penstock Actuator | 1 | PPM | 2014-05-03 | 2014-05-03 |  | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
836 | 2014-05-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-05-03 | 2014-05-03 |  | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser. | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser.
837 | 2014-05-01 | FST | FST 1-4 | FST 1-4 | 4 | PPM | 2014-05-04 | 2014-05-04 |  | Clean the Chanel, Adjust the brushes. | Clean the Chanel, Adjust the brushes.
838 | 2014-05-01 | FST | FST Motors & Gear Boxes | FST Motors & Gear Boxes | 4 | PPM | 2014-05-04 | 2014-05-04 |  | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox | Check the Motor running Amps, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox
839 | 2014-05-01 | SLUDGE DIGESTER | MCC 5 | MCC 5 | 1 | PPM | 2014-05-04 | 2014-05-04 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit
840 | 2014-05-01 | TERTIARY EQUIPMENTS | Tertiary Filter | Back Wash Pumps 1 & 2 | 3 | PPM | 2014-05-05 | 2014-05-05 |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
841 | 2014-05-01 | WASH WATER ROOM | Wash Water Room | Chlorine analyser | 1 | PPM | 2014-05-05 | 2014-05-05 |  | Cleaning of the Chlorine analyser in wash water pump room | Cleaning of the Chlorine analyser in wash water pump room
842 | 2014-05-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 & 2 | 3 | PPM | 2014-05-05 | 2014-05-05 |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow. | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
843 | 2014-05-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | FAT Aerators 1 & 2 | 2 | PPM | 2014-05-06 | 2014-05-06 |  | Checking of oil level and oil condition. Perform Run test and Check the Running Amps. | Checking of oil level and oil condition. Perform Run test and Check the Running Amps.
844 | 2014-05-01 | INLET WORKS | Outfall PS | Outfall Pump 1 & 2 | 2 | PPM | 2014-05-06 | 2014-05-06 |  | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps
845 | 2014-05-01 | INLET WORKS | GG Tank | Grit Tank Penstock Actuator 1 & 2 | 1 | PPM | 2014-05-07 | 2014-05-07 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
846 | 2014-05-01 | INLET WORKS | Inlet | Inlet screen Penstock Acuator 1 & 2 | 1 | PPM | 2014-05-07 | 2014-05-07 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
847 | 2014-05-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filter Effluent water Valve 1-5 | 5 | PPM | 2014-05-08 | 2014-05-08 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
848 | 2014-05-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Air Valve 1-5 | 5 | PPM | 2014-05-08 | 2014-05-08 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
849 | 2014-05-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Valve 1-5 | 5 | PPM | 2014-05-08 | 2014-05-08 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
850 | 2014-05-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash water Valve 1-5 | 5 | PPM | 2014-05-08 | 2014-05-08 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
851 | 2014-05-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Influent Valve 1-5 | 5 | PPM | 2014-05-08 | 2014-05-08 |  | Cleaning the out body for actuator, Cleaning the work place. | Cleaning the out body for actuator, Cleaning the work place.
852 | 2014-05-01 | INLET WORKS | GG Tank | Air Compressor | 1 | PPM | 2014-05-10 | 2014-05-10 |  | Clean the air filter, Clean the Compressor Unit | Clean the air filter, Clean the Compressor Unit
853 | 2014-05-01 | INLET WORKS | GG Tank | Air lift pump 1 & 2 | 2 | PPM | 2014-05-10 | 2014-05-10 |  | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves. | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves.
854 | 2014-05-01 | INLET WORKS | GG Tank | GG Blower 1, 2 & 3 | 3 | PPM | 2014-05-10 | 2014-05-10 |  | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves. | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves.
855 | 2014-05-01 | AERATION | Blower Room | Aeration Blower A & B | 2 | PPM | 2014-05-11 | 2014-05-11 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
856 | 2014-05-01 | AERATION | Blower Room | Aeration Blower C & D | 2 | PPM | 2014-05-11 | 2014-05-11 |  | Clean the complete blower and screens, Check the Air Filter and Clean, | Clean the complete blower and screens, Check the Air Filter and Clean,
857 | 2014-05-01 | AERATION | Blower Room | Aeration Blower D | 1 | PM | 2014-05-12 | 2014-05-12 |  | Removal of the blower electrical motor Cleaning of the motor stator Replacement of the motor bearing Mounting and fixing of the repaired blower motor | Removal of the blower electrical motor
858 | 2014-05-01 | FST | FST 1-4 | Bell Mouth Actuators | 4 | PPM | 2014-05-12 | 2014-05-12 |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place. | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
859 | 2014-05-01 | AERATION | ATLs | IRP 1, 2 & 3 | 3 | PPM | 2014-05-12 | 2014-05-12 |  | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains
860 | 2014-05-01 | SLUDGE DIGESTER | Aerobic sludge digester | Decanter valve | 1 | PPM | 2014-05-13 | 2014-05-13 |  | Hose down decanter unit checking of the valve gearbox | Hose down decanter unit checking of the valve gearbox
861 | 2014-05-01 | FST | FST | Level Sensors | 4 | PPM | 2014-05-14 | 2014-05-14 |  | Removed the DO Sensors , Completely Cleaned & Re-Installed. | Removed the DO Sensors , Completely Cleaned & Re-Installed.
862 | 2014-05-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PPM | 2014-05-14 | 2014-05-14 |  | Cleaning of the blowers and blowers room. Cleaning of the air filter, Check the gear oil. Check the condition and tightness of the Blower V-Belts. Clean the screens, Clean the blower unit. | Cleaning of the blowers and blowers room. Cleaning of the air filter, Check the gear oil. Check the condition and tightness of the Blower V-Belts. Clean the screens, Clean the blower unit.
863 | 2014-05-01 | LV/GEN SET | LV Panel | Gen-set | 1 | PPM | 2014-05-15 | 2014-05-15 |  | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant. | Checking and Running the generator for 30 minutes Clean the Engine & Generator room. Checking the Oil and Coolant.
864 | 2014-05-01 | TOXIC HOLDING TANK | Sludge Holding Tank | Submersible Aerator 1 | 1 | PPM | 2014-05-15 | 2014-05-15 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the Aerator
865 | 2014-05-01 | TOXIC HOLDING TANK | Toxic Holding Tank | Submersible Aerator 1 & 2 | 2 | PPM | 2014-05-15 | 2014-05-15 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the Aerator
866 | 2014-05-01 | INLET WORKS | MCC 2 | MCC 2 | 1 | PPM | 2014-05-17 | 2014-05-17 |  | Cleaning of the MCC panel, Checking of the terminals connections. | Cleaning of the MCC panel, Checking of the terminals connections.
867 | 2014-05-01 | LV/GEN SET | LV Panel | LV panel | 1 | PPM | 2014-05-18 | 2014-05-18 |  | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit | Cleaning of the LV panel, checking the temperature of the bus bar and cable connections and A/C unit
868 | 2014-05-01 | WASH WATER ROOM | Wash Water Room | Wash water Panel | 1 | PPM | 2014-05-18 | 2014-05-18 |  | Cleaning of the panel, Check the tightness of the terminal connection and check the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the panel, Check the tightness of the terminal connection and check the A/C unit Replacement of the fused Panel Indication Lamps
869 | 2014-05-01 | WASH WATER ROOM | Wash Water Room | wash water Pumps | 3 | PPM | 2014-05-18 | 2014-05-18 |  | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp. | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp.
870 | 2014-05-01 | WASH WATER ROOM | Wash Water Room | Wash water room | 1 | PPM | 2014-05-18 | 2014-05-18 |  | Cleaning of electrical panel Clean the Wash water room | Cleaning of electrical panel Clean the Wash water room
871 | 2014-05-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Fixed Aerator 1 & 2 | 2 | PPM | 2014-05-19 | 2014-05-19 |  | Hose down turbine deflection shield, floats and structural beams. | Hose down turbine deflection shield, floats and structural beams.
872 | 2014-05-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Floating Aerator 2 & 3 | 2 | PPM | 2014-05-19 | 2014-05-19 |  | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound. | Checking the condition of Aerator holding fixtures, Check the Running Amps, And Check for abnormal sound.
873 | 2014-05-01 | STORM WATER PS | STORM WATER PS | MCC 8 | 1 | PPM | 2014-05-19 | 2014-05-19 |  | Checking the temperature of the bus bar and cleaning the control panel | Checking the temperature of the bus bar and cleaning the control panel
874 | 2014-05-01 | STORM WATER PS | Storm Water Pumps | Storm Water Pump 1, 2, & 3 | 3 | PPM | 2014-05-19 | 2014-05-19 |  | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. Perform Run Test for the 3 pumps
875 | 2014-05-01 | AERATION | ATL 1 | ATL 2-Mix 1-4 | 4 | PPM | 2014-05-20 | 2014-05-20 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
876 | 2014-05-01 | AERATION | ATL 2 | ATL 3-Mix 1-4 | 4 | PPM | 2014-05-20 | 2014-05-20 |  | Checking the running Amp. Wash the Hoist Chains. | Checking the running Amp. Wash the Hoist Chains.
877 | 2014-05-01 | AERATION | ATLs | Air Flow Meter | 12 | PPM | 2014-05-20 | 2014-05-20 |  | Clean the Equipments completely & Check the Flow meter readings. | Clean the Equipments completely & Check the Flow meter readings.
878 | 2014-05-01 | AERATION | ATLs | ATL 1-Mix 1-4 | 16 | PPM | 2014-05-21 | 2014-05-21 |  | Clean the Complete Junction Boxes and check the tightness condition of the wires inside the JBs. | Clean the Complete Junction Boxes and check the tightness condition of the wires inside the JBs.
879 | 2014-05-01 | AERATION | ATL 3 | ATL 4-Mix 1-4 | 4 | PPM | 2014-05-21 | 2014-05-21 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
880 | 2014-05-01 | AERATION | ATL 4 | ATL 4-Mix 1-4 | 4 | PPM | 2014-05-21 | 2014-05-21 |  | Checking the running Amp. Wash the Hoist Chains | Checking the running Amp. Wash the Hoist Chains
881 | 2014-05-01 | AERATION | ATLs | DO Sensors | 12 | PPM | 2014-05-21 | 2014-05-21 |  | Remove / Lift up the Sensor unit and clean completely the unit and lower down. | Remove / Lift up the Sensor unit and clean completely the unit and lower down.
882 | 2014-05-01 | MCC 7 | Sludge Thickening Plant | MCC 7 | 1 | PPM | 2014-05-21 | 2014-05-21 |  | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals | Cleaning of the MCC7 control panels Checking of terminals and retighten of all loss terminals
883 | 2014-05-01 | AERATION | ATL 1 - 4 | MLSS Sensor | 4 | PPM | 2014-05-21 | 2014-05-21 |  | Removed the MLSS Sensors , Completely Cleaned & Re-Installed. | Removed the MLSS Sensors , Completely Cleaned & Re-Installed.
884 | 2014-05-01 | AERATION | ATLs | Actuators | 12 | PPM | 2014-05-22 | 2014-05-22 |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place. | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
885 | 2014-05-01 | AERATION | Blower Room | Aeration blowers A, B, C & D | 4 | PPM | 2014-05-22 | 2014-05-22 |  | Checking the terminals of all LCP panels for the HV blowers | Checking the terminals of all LCP panels for the HV blowers
886 | 2014-05-01 | AERATION | MCC 3 | MCC 3 | 1 | PPM | 2014-05-22 | 2014-05-22 |  | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit | Cleaning of the MCC panel, Checking of the terminals connections and checking the A/C unit
887 | 2014-05-01 | MCC 7 | Sludge Thickening Plant | Manual Dosing Plant | 1 | PPM | 2014-05-24 | 2014-05-24 |  | Clean the Polymer Mixer and Mixing Tank Completely | Clean the Polymer Mixer and Mixing Tank Completely
888 | 2014-05-01 | TERTIARY EQUIPMENTS | MCC 6 | MCC 6 | 1 | PPM | 2014-05-24 | 2014-05-24 |  | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps | Cleaning of the MCC panel, Checking of the terminal connection and checking the A/C unit Replacement of the fused Panel Indication Lamps
889 | 2014-05-01 | MCC 7 | Sludge Thickening Plant | Polymer Dosing Plant | 1 | PPM | 2014-05-24 | 2014-05-24 |  | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water | Clean the Polymer Feed hopper. Clean the Mixing Tank. Clean the entire plant Floor with wash water
890 | 2014-05-01 | SLUDGE DIGESTER | Aerobic Sludge Digester | Sludge Transfer Pumps | 2 | PPM | 2014-05-24 | 2014-05-24 |  | Checking and cleaning of the lifting chains. checking NRV. | Checking and cleaning of the lifting chains. checking NRV.
891 | 2014-05-01 | MCC 7 | Sludge Thickening Plant | Drain Belt 1 & 2 | 2 | PM | 2014-05-26 | 2014-05-26 |  | Cleaning of the NRV replacement of the side nylon rubber mounted on the thickener | Cleaning of the NRV
892 | 2014-05-01 | RLPS | RLPS PS | RLPS Pump 1,2 & 3 | 3 | PPM | 2014-05-26 | 2014-05-26 |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps
893 | 2014-05-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | CM | 2014-05-27 | 2014-05-27 |  | Repair of: - Ejectors No. 2 and 3, - Vaccum switchs No. 2 and 3, - Primary differential pressure regulator No. 2 and 3, - replacement of the damaged hoses and fittings. | Repair of:
894 | 2014-05-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | CM | 2014-05-27 | 2014-05-27 |  | Repair of: - Ejectors No. 2 and 3, - Vaccum switchs No. 2 and 3, - Primary differential pressure regulator No. 2 and 3, - replacement of the damaged hoses and fittings. | - Ejectors No. 2 and 3
895 | 2014-05-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | CM | 2014-05-27 | 2014-05-27 |  | Repair of: - Ejectors No. 2 and 3, - Vaccum switchs No. 2 and 3, - Primary differential pressure regulator No. 2 and 3, - replacement of the damaged hoses and fittings. | - Vaccum switchs No. 2 and 3
896 | 2014-05-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | CM | 2014-05-27 | 2014-05-27 |  | Repair of: - Ejectors No. 2 and 3, - Vaccum switchs No. 2 and 3, - Primary differential pressure regulator No. 2 and 3, - replacement of the damaged hoses and fittings. | - Primary differential pressure regulator No. 2 and 3
897 | 2014-05-01 | CHLORINATION | Chlorination Room | Chlorination Panel | 1 | CM | 2014-05-27 | 2014-05-27 |  | Repair of: - Ejectors No. 2 and 3, - Vaccum switchs No. 2 and 3, - Primary differential pressure regulator No. 2 and 3, - replacement of the damaged hoses and fittings. | - replacement of the damaged hoses and fittings.
898 | 2014-05-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-05-28 | 2014-05-28 |  | Cleaning the chlorine room, Check the booster pumps. | Cleaning the chlorine room, Check the booster pumps.
899 | 2014-05-01 | CHLORINATION | Chlorination Room | Chlorination System | 1 | PPM | 2014-05-28 | 2014-05-28 |  | Clean the Chlorine room, Check the Safety device for Chlorine gas leaks. | Clean the Chlorine room, Check the Safety device for Chlorine gas leaks.
900 | 2014-05-01 | MCC 7 | Sludge Thickening Plant | Thick Sludge Pumps | 2 | PPM | 2014-05-28 | 2014-05-28 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
901 | 2014-05-01 | MCC 7 | Sludge Thickening Plant | Thin Sludge Pumps | 2 | PPM | 2014-05-28 | 2014-05-28 |  | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel | Cleaning the stuffing box, motor cooling fan and checking the MCC control panel
902 | 2014-07-01 | MCC 3 | ATL 3 | Actuator 3 | 1 | CM | 2014-07-01 | 2014-07-01 |  | Replace the Fuse and Indication lamp | replace the damaged fuse | 1 | Fuse - 4 A | 1 |  | A.Amir | 0.5
903 | 2014-07-01 | MCC 3 | ATL 3 | Actuator 3 | 1 | CM | 2014-07-01 | 2014-07-01 |  | Replace the Fuse and Indication lamp | replace the damaged panel indication lamp | 2 | indication lamps | 1 |  | A.Amir | 0.5
904 | 2014-07-01 | TERTIARY EQUIPMENTS | MCC 6 | TE Pump 1 | 1 | CM | 2014-07-02 | 2014-07-02 |  | Repair of: - Fix the Head Cover - Fix the Cable dummy hole gland - Give the Cable Connections for the stator and the Cable. - Put Silicone and tight the head Cover. | Fix the Head Cover of the Pump after it was completely cleaned and checked . |  |  |  |  | Lijo | 2
905 | 2014-07-01 | TERTIARY EQUIPMENTS | MCC 6 | TE Pump 1 | 1 | CM | 2014-07-02 | 2014-07-02 |  | Repair of: - Fix the Head Cover - Fix the Cable dummy hole gland - Give the Cable Connections for the stator and the Cable. - Put Silicone and tight the head Cover. | Fix the Cable dummy hole gland with New dummy closers | 1 | Cable dummy closers | 3 |  | A.Amir | 2
906 | 2014-07-01 | TERTIARY EQUIPMENTS | MCC 6 | TE Pump 1 | 1 | CM | 2014-07-02 | 2014-07-02 |  | Repair of: - Fix the Head Cover - Fix the Cable dummy hole gland - Give the Cable Connections for the stator and the Cable. - Put Silicone and tight the head Cover. | Give the Cable Connections from the Stator to the Cable | 2 | Silicone
907 | 2014-07-01 | TERTIARY EQUIPMENTS | MCC 6 | TE Pump 1 | 1 | CM | 2014-07-02 | 2014-07-02 |  | Repair of: - Fix the Head Cover - Fix the Cable dummy hole gland - Give the Cable Connections for the stator and the Cable. - Put Silicone and tight the head Cover. | Put silicone and tight the head cover
908 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | Back wash Pump 2 | 1 | CM | 2014-07-01 | 2014-07-01 |  | Painting Job | Paont the external of the pump completely with epoxy paint |  | Epoxy Paint-Hempel |  |  | Saman + Insan | 2
909 | 2014-07-01 | MCC 6 | MCC 6 | Filteration panel | 1 | CM | 2014-07-07 | 2014-07-07 |  | PLC Display unit was Hanged, checked the supply and re-set | Check the supply voltage to the display unit |  |  |  |  | Er.Ajith + Lijo | 0.5
910 | 2014-07-01 | MCC 6 | MCC 6 | Filteration panel | 1 | CM | 2014-07-07 | 2014-07-07 |  | PLC Display unit was Hanged, checked the supply and re-set | Re-set the display unit |  |  |  |  | Er.Ajith =Lijo | 0.5
911 | 2014-07-01 | MCC 6 | MCC 6 | TE. Filter Blower 2 | 1 | CM | 2014-07-07 | 2014-07-07 |  | Selector switch was damaged | Replace the damaged selector switch in the panel and fix new. | 1 | Selector Switch | 1 |  | A.mir | 0.5
912 | 2014-07-01 | MCC 5 | Sludge Digestor | Floating Aerator 1 | 1 | CM | 2014-07-08 | 2014-07-08 |  | Disconnect the existing cable of FLA-1 from JB and connect the New SA cable and conduct reun test. | Disconnect the Old existing rubber cable of the Floating Aerator No.1 from the JB |  |  |  |  | Er.Nap + Er.Ajith +Mr.Lois | 3
913 | 2014-07-01 | MCC 5 | Sludge Digestor | Floating Aerator 1 | 1 | CM | 2014-07-08 | 2014-07-08 |  | Disconnect the existing cable of FLA-1 from JB and connect the New SA cable and conduct reun test. | Connect the New Cable of the Submersible Aerator (planned to Install). |  |  |  |  | Er.Nap + Er.Ajith + Mr.Lois | 3
914 | 2014-07-01 | MCC 5 | Sludge Digestor | Floating Aerator 1 | 1 | CM | 2014-07-08 | 2014-07-08 |  | Disconnect the existing cable of FLA-1 from JB and connect the New SA cable and conduct reun test. | Adjust the settings in the VFD as oer the New Aerator details. And conduct test run |  |  |  |  | Er.Nap + Er.Ajith + Mr.Lois | 3
915 | 2014-07-01 | WASH WATER ROOM | Wash Water Room | VFD Control | 1 | CM | 2014-07-09 | 2014-07-09 |  | Error display in the Panel, checked and re-set | Check the VFD control and Re-set. |  |  |  |  | Er.Ajith + Lijo | 1
916 | 2014-07-01 | PLANT AREA and Others | Plant Area | All MCCS + Buildings | 1 | CM | 2014-07-09 | 2014-07-09 |  | Ministry Guy from Building Service Maintenance came and Inspect all the Lightings and Building Maintenance needed | Shown to the Ministry Guy about all the Lightings needed for All MCCs and Admin Building and Blower room amd Thickner room |  |  |  |  | Ministry Guy + Er.Ajith | 1
917 | 2014-07-01 | MCC 5 | MCC 5 | Floating Aerator 1 | 1 | CM | 2014-07-09 | 2014-01-09 |  | Replace the Panel Indication lamp | Replace the damaged Panel Indication lamp and fix new | 1 | indication lamps | 1 |  | A.Amir | 0.5
918 | 2014-07-01 | MCC 7 | MCC 7 | A/C | 1 | CM | 2014-07-10 | 2014-07-10 |  | Replace the damaged AC switch | Replace the damaged AC switch and fix the New | 1 | AC Switch | 1 |  | A.Amir | 0.5
919 | 2014-07-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1 | 1 | CM | 2014-07-10 | 2014-07-10 |  | Installation & Commission of the repaired pump | After repair service work lower down the TE Pump, Give the Cable connection in the JB, Arrange the Cables using Cable ties | 1 | Cable ties |  |  | A.Amir | 1
920 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | Back Wash Pump 2 | 1 | CM | 2014-07-10 | 2014-07-10 |  | Installation & Commission of the repaired pump | After repair service work lower down the TE Pump, Give the Cable connection in the JB, Arrange the Cables using Cable ties | 1 | Cable ties | 1 |  | A.Amir | 1
921 | 2014-07-01 | MCC 3 | ATL 1 | ATL 1-Mix 1 | 1 | CM | 2014-07-10 | 2014-07-10 |  | Winding Temp Trip | Winding Temperature Trip was occurred in the MCC panel |  |  |  |  | A.Amir | 1
922 | 2014-07-01 | MCC 3 | ATL 1 | ATL 1-Mix 1 | 1 | CM | 2014-07-10 | 2014-07-10 |  | Winding Temp Trip | Replace the old damaged resistr and fix new | 1 | Resistor | 1 |  | A.Amir | 1
923 | 2014-07-01 | MCC 3 | Blower Room | Aeration Blower D | 1 | CM | 2014-07-19 | 2014-07-19 |  | Installation & Commission | After filling New Grease perform sample run test for Blower D | 1 | Calbe ties |  |  | A,Amir | 2
924 | 2014-07-01 | MCC 3 | Blower Room | Aeration Blower D | 1 | CM | 2014-07-19 | 2014-07-19 |  | Installation & Commission | Arrange the Cable for the Exhaust Fan of the Blower D |  |  |  |  | A.Amir | 2
925 | 2014-07-01 | CHLORINATION | Chlorine drum room | Chlorine drum room |  | CM | 2014-07-19 | 2014-07-19 |  | Gas Leak Alarm, Rectifeid and arrest the Leak | Close the valves and run the exhaust Fans |  |  |  |  | Er.Ajith +Shahbaz | 1
926 | 2014-07-01 | CHLORINATION | Chlorine drum room | Chlorine drum room |  | CM | 2014-07-19 | 2014-07-19 |  | Gas Leak Alarm, Rectifeid and arrest the Leak | Check the valves one by one
927 | 2014-07-01 | CHLORINATION | Chlorine drum room | Chlorine drum room |  | CM | 2014-07-19 | 2014-07-19 |  | Gas Leak Alarm, Rectifeid and arrest the Leak | Arrest the Leak
928 | 2014-07-01 | TERTIARY EQUIPMENTS | MCC 6 | Back wash Pump 2 |  | CM | 2014-07-19 | 2014-07-19 |  | replace the damaged selector switch in the panel and fix new. | Replace the old damaged selector switch and fix New one | 1 | Selector Switch | 1 |  | A.Amir | 0.5
929 | 2014-07-01 | MCC 6 | MCC 6 | A/C |  | CM | 2014-07-10 | 2014-07-10 |  | AC unit tripped, Checked our supply | Ac Tripped, Checked our supply, Found ok. Informed to Mr.Ishaq (AC under warranty by Mr.Ishaq) |  |  |  |  | A.Amir | 1
930 | 2014-07-01 | MCC 3 | ATL 3 | IRP 3 | 1 | CM | 2014-07-22 | 2014-07-22 |  | Hight current trip, reset | Found High current trip in Panel |  |  |  |  | A.Amir | 1
931 | 2014-07-01 | MCC 3 | ATL 3 | IRP 3 | 1 | CM | 2014-07-22 | 2014-07-22 |  | Hight current trip, reset | Reset the panel and try to run, Again trip. Planned to lift up the IRP-3 |  |  |  |  | Lijo | 3
932 | 2014-07-01 | MCC 3 | ATL 3 | IRP 3 | 1 | CM | 2014-07-23 | 2014-07-23 |  | Hight current trip, reset | Found mooring cable broken, informed to mech team and lift up the IRP-3 |  |  |  |  | A.Amir | 3
933 | 2014-07-01 | MCC 3 | ATL 3 | IRP 3 | 1 | CM | 2014-07-23 | 2014-07-23 |  | Hight current trip, reset | Disconnect the cable from JB and Check the Cables (vusual inspection)
934 | 2014-07-01 | MCC 3 | ATL 3 | IRP 3 | 1 | CM | 2014-07-23 | 2014-07-23 |  | Hight current trip, reset | Check the Megger & resistance
935 | 2014-07-01 | MCC 3 | ATL 3 | IRP 3 | 1 | CM | 2014-07-23 | 2014-07-23 |  | Hight current trip, reset | After fixing new ss rope, lower down the Irp and give connection
936 | 2014-07-01 | TOXIC HOLDING TANK | Toxic Holding Tank | Submersible Aerator 1 & 2 | 2 | PPM | 2014-07-03 | 2014-07-03 |  | Check the Steel wire ropes and spray water for the SS ropes, Coduct run test for 15 Minutes, Check the Amphere. | Check the stain less steel ropes and spray pressurized water to clean completely. |  |  |  |  | Lijo +A.Amir+Humayun | 1.5
937 | 2014-07-01 | MCC 2 | MCC 2 | Complete Panel | 1 | PPM | 2014-07-03 | 2014-07-03 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) |  |  |  |  | Lijo +A.Amir+Humayun | 2
938 | 2014-07-01 | LV/GEN SET | LV Panel | Complete Panel | 1 | PPM | 2014-07-05 | 2014-07-05 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) |  |  |  |  | Lijo + A.Amir | 2
939 | 2014-07-01 | MCC 2 | MCC 2 | Complete Panel | 1 | PPM | 2014-07-14 | 2014-07-14 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) |  |  |  |  | Lijo + Samson + A.Amir | 2
940 | 2014-07-01 | WASH WATER ROOM | Wash Water Room | Complete Panel | 1 | PPM | 2014-07-17 | 2014-07-17 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Amps of the Pump Check the vibration of the Pump (if not satisfied mention it) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Amps of the Pump Check the vibration of the Pump (if not satisfied mention it) |  |  |  |  | Lijo+ A.Amir | 3
941 | 2014-07-01 | MCC 7 | MCC 7 | Complete Panel |  | PPM | 2014-07-20 | 2014-07-20 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room | 1 | Selector Switch | 1 |  | Lijo + A.Amir | 3
942 | 2014-07-01 | MCC 4 | MCC 4 | Complete Panel | 1 | PPM | 2014-07-22 | 2014-07-22 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) |  |  |  |  | Lijo + A.Amir | 4
943 | 2014-07-01 | MCC 6 | MCC 6 | Complete Panel | 1 | PPM | 2014-07-26 | 2014-07-26 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | 1 | Selector Switch | 1 |  | Lijo + A.Amir | 3
944 | 2014-07-01 | MCC 3 | MCC 3 | Complete Panel | 1 | PPM | 2014-07-27 | 2014-07-27 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) |  |  |  |  | Lijo + A.Amir | 4
945 | 2014-07-01 | CHLORINATION | CHLORINATION Panel | Complete Panel | 1 | PPM | 2014-07-21 | 2014-07-21 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) |  |  |  |  | Lijo + A.Amir | 1
946 | 2014-07-01 | MCC 5 | MCC 5 | Complete Panel | 1 | PPM | 2014-07-31 | 2014-07-31 |  | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) | Check the panel Indication Lamps Check the Push buttons in the Panels Check the Selector Switches in the Panel (replace if needed) Open the Panel and Clean Inside Check the Tightness of the Connections and do if needed Check working Condition of AC inside the Control rooms Check the Lightings Inside the Control room Remove the debris found inside the Control room Check the Ampheres of the Equipments connected (mention if abnormal) |  |  |  |  | Lijo + A.Amir | 4
947 | 2014-07-01 | MCC 5 | Sludge Digestor | New Sub.Aerator | 1 | CM | 2014-07-05 | 2014-07-05 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.1 | Check the Panel ratings |  |  |  |  | Er.Nap + Er.Ajith +Lijo | 2
948 | 2014-07-01 | MCC 5 | Sludge Digestor | New Sub.Aerator | 1 | CM | 2014-07-05 | 2014-07-05 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.2 | Check the VFD control and their ratings |  |  |  |  | Er.Nap + Er.Ajith +Lijo | 2
949 | 2014-07-01 | MCC 5 | Sludge Digestor | New Sub.Aerator | 1 | CM | 2014-07-05 | 2014-07-05 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.3 | Check the supply volts and protection details |  |  |  |  | Er.Nap + Er.Ajith +Lijo | 2
950 | 2014-07-01 | SLUDGE DIGESTER | Sludge Digestor | Submersible Aerator 1 | 1 | CM | 2014-07-05 | 2014-07-05 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.4 | Check the Megger & resistance |  |  |  |  | Er.Nap + Er.Ajith +Mr.Lois | 1.5
951 | 2014-07-01 | SLUDGE DIGESTER | Sludge Digestor | Submersible Aerator 1 | 1 | CM | 2014-07-05 | 2014-07-05 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.5 | lower down the aerator and fix the morring cables |  |  |  |  | Er.Nap + Er.Ajith + Mr.Lois | 1.5
952 | 2014-07-01 | MCC 5 | Sludge Digestor | Submersible Aerator 1 | 1 | CM | 2014-07-10 | 2014-07-10 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.6 | Give connection and conduct run test and check the starting and running Amphere |  |  |  |  | Lijo +A,Amir+Saman+ Rohan+ bandula | 3
953 | 2014-07-01 | MCC 5 | Sludge Digestor | Submersible Aerator 1 | 1 | CM | 2014-07-13 | 2014-07-14 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.7 | Install the protection relay inside the panel as per the new drawing given by Er.Nap (Ministry) |  |  |  |  | Lijo + Samson + A.Amir | 3
954 | 2014-07-01 | MCC 5 | Sludge Digestor | Submersible Aerator 1 | 1 | CM | 2014-07-13 | 2014-07-14 |  | Installation of New Sub.Aerator instead of damaged Floating Aerator.No.8 | Give the control connections to the protection relay. |  |  |  |  | Lijo + Samson + A.Amir | 3
955 | 2014-07-01 | INLET WORKS | Inlet | Inlet screen Penstock Acuator 1 & 2 | 1 | PPM | 2014-07-12 |  |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
956 | 2014-07-01 | INLET WORKS | GG Tank | Grit Tank Penstock Actuator 1 & 2 | 1 | PPM | 2014-07-12 |  |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
957 | 2014-07-01 | INLET WORKS | GG Tank | Air lift pump 1 & 2 | 2 | PPM | 2014-07-12 |  |  | Cleaning the air Filter and Checking the Air Pipe line & Check the Safety Valves.
958 | 2014-07-01 | INLET WORKS | GG Tank | Air lift pump 2 | 1 | PPM | 2014-07-08 |  |  | Airlift pump line was found blocked and the blockage was removed and rectified.
959 | 2014-07-01 | INLET WORKS | Inlet | Fine Screen 1 & 2 | 2 | PPM | 2014-07-12 |  |  | Cleaning of the inlet screens. Check and Clean the nozzles, Check and Clean the Level sensors and Air Tubes
960 | 2014-07-01 | INLET WORKS | GG Tank | GG Blower 1, 2 & 3 | 3 | PPM | 2014-07-09 |  |  | Cleaning of the Air Filter Check the Air Pipeline and Valves. Check the Safety valves.
961 | 2014-07-01 | INLET WORKS | GG Tank | Grease Scraper 1 & 2 | 2 | PPM | 2014-07-09 |  |  | Check oil level , Check the chain scraper and plummer block bearing condition and scraper paddle. Lubricate the scraper chain and rails.
962 | 2014-07-01 | INLET WORKS | Outfall PS | Outfall Pump 1 & 2 | 2 | PPM | 2014-07-25 |  |  | Clean/Spray with pressurized water for the hoisting chains, Perform run test for the pumps
963 | 2014-07-01 | INLET WORKS | Inlet | Grit Classifier | 1 | PPM | 2014-07-09 |  |  | Checking of oil level and geared motor unit and solenoid valve operation. Cleaning the champer, cleaning the grit container
964 | 2014-07-01 | INLET WORKS | GG Tank | Air Lift Compressor | 1 | PPM | 2014-07-12 |  |  | Clean the air filter, Clean the Compressor Unit
965 | 2014-07-01 | INLET WORKS | MCC 2 | A/C |  | PPM | 2014-07-03 |  |  | Check the working Condition of AC, Check the Cooling of the AC. Clean the Filter, Check the switch.
966 | 2014-07-01 | INLET WORKS | MCC 2 | MCC 2 | 1 | PPM | 2014-07-03 |  |  | Cleaning of the MCC panel, Check the Panel Indication Lamps, Check the Push buttons in the Panel, Check the Selector switches in the Panel, Open the Panel and clean inside, check the tighntness of the conectiona and re-tight if needed, Remove the debris from the MCC room
968 | 2014-07-01 | AERATION | ATL 1 | ATL 2-Mix 1-4 | 4 | PPM | 2014-07-13 |  |  | Checking the running Amp. Wash the Hoist Chains, Check the Emergency Push Buttons (near to the tank), clean the JBs, Check the terminal connections.
969 | 2014-07-01 | AERATION | ATL 2 | ATL 3-Mix 1-4 | 4 | PPM | 2014-07-13 |  |  | Checking the running Amp. Wash the Hoist Chains, Check the Emergency Push Buttons (near to the tank), clean the JBs, Check the terminal connections.
970 | 2014-07-01 | AERATION | ATL 3 | ATL 4-Mix 1-4 | 4 | PPM | 2014-07-13 |  |  | Checking the running Amp. Wash the Hoist Chains, Check the Emergency Push Buttons (near to the tank), clean the JBs, Check the terminal connections.
971 | 2014-07-01 | AERATION | ATL 4 | ATL 4-Mix 1-4 | 4 | PPM | 2014-07-13 |  |  | Checking the running Amp. Wash the Hoist Chains, Check the Emergency Push Buttons (near to the tank), clean the JBs, Check the terminal connections.
973 | 2014-07-01 | AERATION | ATLs | IRP | 1 | PPM | 2014-07-03 |  |  | Cleaning the Hoist Chains with pressurized water Check the Condition of the Hoist Chains
974 | 2014-07-01 | AERATION | ATLs | Air Flow Meter | 12 | PPM | 2014-07-26 |  |  | Clean the Equipments completely & Check the Flow meter readings.
975 | 2014-07-01 | AERATION | ATLs | Actuators | 12 | PPM | 2014-07-26 |  |  | Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
976 | 2014-07-01 | AERATION | ATLs | IRP 3 | 1 | PM | 2014-07-10 |  |  | Found the lifting SS rope was broken, replaced it with 8 Meter new SS rope. And lower down the IRP |  |  | SS rope - 8 mtr
977 | 2014-07-01 | AERATION | Blower Room | Aeration Blower A & B | 2 | PPM | 2014-07-19 |  |  | Clean the complete blower and screens, Check the Air Filter and Clean,
978 | 2014-07-01 | AERATION | Blower Room | Aeration Blower C & D | 2 | PPM | 2014-07-19 |  |  | Clean the complete blower and screens, Check the Air Filter and Clean,
979 | 2014-07-01 | AERATION | Blower Room | Aeration Blower D | 1 | PPM | 2014-07-15 |  |  | Replace the Old Grease of the Blower motor bearings, clean completely and fill with new Grease
980 | 2014-07-01 | AERATION | Blower Room | Aeration blowers A, B, C & D | 4 | PPM | 2014-07-19 |  |  | Checking the terminals of all LCP panels for the HV blowers, clean completely the Panel.
981 | 2014-07-01 | AERATION | MCC 3 | Mix 1 | 1 | CM | 2014-07-10 |  |  | Gound winding temperature trip, Checked and found the resistor connected was damaged. Replaced it with New and Now working good. |  |  | Resistor - 1 nos
982 | 2014-07-01 | AERATION | MCC 3 | A/C |  | PPM | 2014-07-27 |  |  | Check the working Condition of AC, Check the Cooling of the AC. Clean the Filter, Check the switch.
983 | 2014-07-01 | AERATION | MCC 3 | MCC 3 | 1 | PPM | 2014-07-27 |  |  | Cleaning of the MCC panel, Check the Panel Indication Lamps, Check the Push buttons in the Panel, Check the Selector switches in the Panel, Open the Panel and clean inside, check the tighntness of the conectiona and re-tight if needed, Remove the debris from the MCC room
985 | 2014-07-01 | FST | FST 1-4 | FST 1-4 | 4 | PPM | 2014-07-20 |  |  | Clean the Chanel, Adjust the brushes.
986 | 2014-07-01 | FST | FST Motors with Gear Box | FST Motors with Gear Box | 4 | PM | 2014-07-20 |  |  | Check the Motor running Amps, Check for any abnormal noise in the Motor, Check the Gear Box Oil Condition and Oil Level Replacement of oil for the clarifier main gearbox
987 | 2014-07-01 | FST | RAS/SAS PS | RAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-07-26 |  |  | Cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and flow meters.
988 | 2014-07-01 | FST | RAS/SAS PS | RAS/SAS Penstock Actuator | 1 | PPM | 2014-07-24 |  |  | Lubricating the thread bar, Cleaning the actuator motor and body, Exercise the manual valve, Cleaning the work place.
989 | 2014-07-01 | FST | RAS/SAS PS | SAS pumps 1, 2, 3 & 4 | 4 | PPM | 2014-07-24 |  |  | cleaning with pressurized water the hoisting chains, valve chamber. Checking the control panel and level Analyser.
990 | 2014-07-01 | FST | FST | Level Sensors | 4 | PPM | 2014-07-26 |  |  | Removed the Level Sensors, Completely Cleaned & Re-Installed. Check the readings in the display unit and the Panel Screen, found same.
991 | 2014-07-01 | FST | MCC 4 | A/C | 1 | PPM | 2014-07-22 |  |  | Check the working Condition of AC, Check the Cooling of the AC. Check the switch.
992 | 2014-07-01 | FST | MCC 4 | MCC 4 | 1 | PPM | 2014-07-22 |  |  | Cleaning of the MCC panel, Check the Panel Indication Lamps, Check the Push buttons in the Panel, Check the Selector switches in the Panel, Open the Panel and clean inside, check the tighntness of the conectiona and re-tight if needed, Remove the debris from the MCC room
994 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Influent Valve 1-5 | 5 | PPM | 2014-07-08 |  |  | Cleaning the out body for actuator, Cleaning the work place.
995 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash water Valve 1-5 | 5 | PPM | 2014-07-08 |  |  | Cleaning the out body for actuator, Cleaning the work place.
996 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash Air Valve 1-5 | 5 | PPM | 2014-07-08 |  |  | Cleaning the out body for actuator, Cleaning the work place.
997 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filters Dirty Backwash water Valve 1-5 | 5 | PPM | 2014-07-08 |  |  | Cleaning the out body for actuator, Cleaning the work place.
998 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | TE. Filter Effluent water Valve 1-5 | 5 | PPM | 2014-07-08 |  |  | Cleaning the out body for actuator, Cleaning the work place.
999 | 2014-07-01 | TERTIARY EQUIPMENTS | TF Blower Room | TE. Filter Blowers 1 & 2 | 2 | PPM | 2014-07-23 |  |  | Cleaning of the blowers and blowers room. Cleaning of the air filter, Check the gear oil. Check the condition and tightness of the Blower V-Belts. Clean the screens, Clean the blower unit.
1000 | 2014-07-01 | FST | FST 1-4 | Bell Mouth Actuators | 4 | PPM | 2014-07-05 |  |  | Cleaning the out body for actuator, Checking the grease condition, Cleaning the work place.
1001 | 2014-07-01 | TERTIARY EQUIPMENTS | TE. PS. | TE Pump 1, 2 & 3 | 2 | PPM | 2014-07-17 |  |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
1002 | 2014-07-01 | TERTIARY EQUIPMENTS | Tertiary Filter | Back Wash Pumps 1 & 2 | 2 | PPM | 2014-07-10 |  |  | Cleaning with pressurized water the hoisting chains. Checking the Running Amps and Flow.
1003 | 2014-07-01 | TERTIARY EQUIPMENTS | MCC 6 | A/C | 1 | PPM | 2014-07-26 |  |  | Check the working Condition of AC, Check the Cooling of the AC. Check the switch.
1004 | 2014-07-01 | TERTIARY EQUIPMENTS | MCC 6 | MCC 6 | 1 | PPM | 2014-07-26 |  |  | Cleaning of the MCC panel, Check the Panel Indication Lamps, Check the Push buttons in the Panel, Check the Selector switches in the Panel, Open the Panel and clean inside, check the tighntness of the conectiona and re-tight if needed, Remove the debris from the MCC room | Damaged Selector switch was replaced by New One |  | Damaged Selector switch was replaced by New One
1006 | 2014-07-01 | RLPS | RLPS PS | RLPS Pump 1,2 & 3 | 3 | PPM | 2014-07-25 |  |  | Checking the condition of hoisting chains and cleaning the control panel. and Perform Run Test for the 3 pumps
1008 | 2014-07-01 | WASH WATER ROOM | Wash Water Room | Chlorine Analyser | 1 | PPM | 2014-07-04 |  |  | Cleaning of the Chlorine analyser in wash water pump room
1009 | 2014-07-01 | WASH WATER ROOM | Wash Water Room | Wash water Panel | 1 | PPM | 2014-07-17 |  |  | Cleaning of the panel, Check the tightness of the terminal connection and check the A/C unit Replacement of the fused Panel Indication Lamps
1010 | 2014-07-01 | WASH WATER ROOM | Wash Water Room | wash water Pumps | 3 | PPM | 2014-07-17 |  |  | Check the running condition of the Pumps, Observe it there is any Noise, Check the running Amp.
|  | CHLORINATION | CHLORINATION Panel | Aeration blower A
|  | INLET_WORKS | Chlorine drum room | Air Lift Compressor
|  | LOCATION | AREA | EQUIPMENT

## Area
LOCATION | AERATION | CHLORINATION | FST | INLET_WORKS | LV_GEN_SET | MCC_2 | MCC_3 | MCC_4 | MCC_5 | MCC_6 | MCC_7 | PLANT_AREA_and_Others | RLPS | SLUDGE_DIGESTER | STORM_WATER_PS | TERTIARY_EQUIPMENTS | TOXIC_HOLDING_TANK | WASH_WATER_ROOM
AREA | MCC 3 | Chlorine drum room | MCC 4 | MCC 2 | LV Panel | MCC 2 | ATL 3 | MCC 4 | MCC 5 | MCC 6 | MCC 7 | Garden | RLPS PS | Sludge Digester | MCC 8 | MCC 6 | Toxic Holding Tank | MCC 5
| MCC 3 | CHLORINATION Panel | FST 1-4 | GG Tank |  |  | Blower Room |  | Sludge Digestor |  | Sludge Thickening Plant | Laboratory |  | MCC 5 | STORM WATER PS | Out Fall Valve (to the sea) |  | Wash Water Room
| ATLs | Chlorination Room | FST 1-4 | Inlet |  |  | MCC 3 |  |  |  | Sludge Holding Tank | LV panel |  |  | Storm Water Pumps | TE. PS.
| ATLs |  | FST 2 | Outfall PS |  |  | ATL 1 |  |  |  |  | Main Entrance |  |  |  | Tertiary Filter
| ATLs |  | FST 1 | G1 Pumping Station | [7 empty] | Plant Area |  |  |  | TF Blower Room
| ATLs |  | FST 1 & 3 | [8 empty] | SCADA room
| ATLs |  | FST 2 | [8 empty] | Security Cabin
| ATLs |  | FST 3
| ATLs |  | FST 4
| ATLs |  | FST Motors & Gear Boxes
| ATL 1 - 4 |  | FST Motors with Gear Box
| Blower Room |  | FST
RAS/SAS PS

## Eq
Equipment
A/C
Actuator 3
Actuators
Actuators 1-3
Admin Building
Aeration blower A
Aeration Blower A & B
Aeration blower A & D
Aeration Blower B
Aeration blower B & C
Aeration blower C
Aeration Blower C & D
Aeration Blower D
Aeration blowers A, B, C & D
Air Compressor
Air Flow Meter
Air Lift Compressor
Air lift pump 1 & 2
Air lift pump 2
All MCCS + Buildings
ATL 4
Back Wash Pump 1
Back wash Pump 2
Back Wash Pumps 1 & 2
Bell Mouth Actuators
Chlorination panel
Chlorination Room
Chlorination System
Chlorinator 1
Chlorinator 2
Chlorinator 3
Chlorine analyser
Chlorine drum room
Complete Panel
Decanter valve
Distribution chamber gate valves
DO Sensors
Drain Belt 1 & 2
drainage valve
FAT aerators 1 & 2
Filteration panel
Fine screen 1 & 2
Fixed aerator 1
Fixed Aerator 1 & 2
Fixed Aerator 2
Fixed aerator 3
Floating Aerator 1
Floating Aerator 1 & 2
Floating aerator 1, 2 & 3
Floating Aerator 2
Floating Aerator 2 & 3
Floating aerator 3
FST 1
FST 1 & 3
FST 1-4
FST 2
FST 3
FST 4
FST Motors & Gear Boxes
FTFT Penstock, Actuator
Garden
Gear Box
Gen-set
GG Blower 1
GG blower 1, 2 & 3
GG blower 2
Grease scraper 1 & 2
Grease scraper 2
Grease scraper motor 1 & 2
Grit classifier
Grit Tank Penstock Actuator 1 & 2
Inlet screen Penstock Acuator 1 & 2
IRP
IRP 1
IRP 1, 2 & 3
IRP 3
Landscape & garden
Level Sensors
LV panel
Manual Dosing Plant
MCC 3
MCC 4
MCC 5
MCC 6
MCC 7
MCC 8
MCC 2
ATL 1-Mix 1
ATL 2-Mix 1
ATL 4-Mix 1
Mix 1
ATL 1-Mix 2
ATL 3-Mix 2
ATL 4-Mix 2
ATL 1-Mix 3
ATL 1-Mix 4
ATL 2-Mix 4
ATL 3-Mix 4
ATL 4-Mix 4
ATL 3-Mix 1-3-4
ATL 1-Mix 1-4
ATL 2-Mix 1-4
ATL 3-Mix 1-4
ATL 4-Mix 1-4
ATL 2-Mix 2-3-4
MLSS Sensor
Motor & Gear Box
New Sub.Aerator
NS-STP Main Gate
NS-STP Security Cabin - Water Tank
Outfall Pump 1 & 2
pH Meter in G1 Line
Polymer Dosing Plant
RAS pumps 1
RAS pumps 1, 2, 3 & 4
RAS pumps 3
RAS pumps 4
RAS/SAS Penstock Actuator
RLPS pump 1
RLPS Pump 1,2 & 3
RLPS pump 2
RLPS pump 3
RLPS pumping station
RLPS Tank
Road, Land Scape & Admin Building
SAS pumps 1, 2, 3 & 4
SAS pumps 2
Sludge transfer pumps
Solenoid Valve & Timer
Storm Water Pump 1, 2, & 3
Street Lighting
Submersible Aerator 1
Submersible Aerator 1 & 2
TE Pump 1
TE Pump 1 & 2
TE Pump 1 & 3
TE Pump 1, 2 & 3
TE Pump 3
TE. Filter 4, Valve 4
TE. Filter Blower 1
TE. Filter Blower 2
TE. Filter Blowers 1 & 2
TE. Filter Blowers Air Flow Actuator
TE. Filter Effluent water Valve 1-5
TE. filter inlet area
TE. Filters Dirty Backwash Air Valve 1-5
TE. Filters Dirty Backwash Valve 1-5
TE. Filters Dirty Backwash water Valve 1-5
TE. Filters Influent Valve 1-5
TE. Pumping station
Thick sludge pumps
Thin sludge pumps
VFD Control
Wash water Panel
Wash water pump 2
wash water Pumps
Wash water room