## Formulas GT
Ambient Pressure
| Power | Net Heatrate
P (bar) | Correction Factor
0.97 | 0.85428 | 1.0335
0.99 | 0.8644 | 1.0276
1.01 | 0.902 | 1.0297
1.013 | 0.90465 | 1.029
1.03 | 0.91088 | 1.0235

## Efficiency
| Guaranteed | Measured |  | FDM Corrector Ratio |  |  | Compressor GT 1
Input parameter | Value | Value | Unit | Power | Net Heat Rate |  | Quantity | Value | Unit
Ambient Pressure | 1.013 | 1.0038 | bar | 1.016 | 0.99993 | INPUT | DP Before Compressor Inlet | 4.694 | mbar
[7 empty] | Compressor Inlet Pressure | 4.693 | bara
[7 empty] | Compressor Outlet Pressure | 9.7575 | bara
[7 empty] | Compressor Inlet Temperature | 30.225 | °C
[7 empty] | Compressor Outlet Temperature | 355.3666 | °C
[7 empty] | Quantity | Value | Unit
[6 empty] | RESULT | Efficiency | 85.6235 | %

## Raw Data
Start | 2017-05-24 15:00
End | 2017-05-24 16:00
|  |  | P0WST01CP001_XQ01 | P1MBL10CP010_XQ01 | P1MBA12FP100_ZQ03 | P1MBA11CT901_ZQ01 | P1MBA12CT901_ZQ01
|  |  | Ambient Pressure | Compressor Inlet Pressure GT1 | Compressor Outlet Pressure GT1 | Compressor Inlet Temperature GT1 | Compressor Outlet Temperature GT1
|  |  | 1003.8455 | 4.694 | 9.7575 | 30.225 | 355.3666
|  | 2017-05-24 15:00 | 1003.8524 | 4.7024 | 9.7384 | 30.2905 | 355.2187
|  | 2017-05-24 15:01 | 1003.8423 | 4.6968 | 9.738 | 30.3071 | 355.1349
|  | 2017-05-24 15:02 | 1003.8457 | 4.6992 | 9.7377 | 30.3238 | 355.0859
|  | 2017-05-24 15:03 | 1003.8401 | 4.7299 | 9.7373 | 30.3404 | 355.2328
|  | 2017-05-24 15:04 | 1003.8735 | 4.7631 | 9.7369 | 30.3571 | 355.4101
|  | 2017-05-24 15:05 | 1003.8574 | 4.7719 | 9.7366 | 30.3737 | 355.4569
|  | 2017-05-24 15:06 | 1003.9001 | 4.6739 | 9.7362 | 30.3904 | 355.3909
|  | 2017-05-24 15:07 | 1003.9497 | 4.6815 | 9.7358 | 30.407 | 355.337
|  | 2017-05-24 15:08 | 1003.9423 | 4.689 | 9.7355 | 30.4237 | 355.3462
|  | 2017-05-24 15:09 | 1003.9438 | 4.6888 | 9.7351 | 30.4403 | 355.3643
|  | 2017-05-24 15:10 | 1003.9328 | 4.6837 | 9.7358 | 30.457 | 355.3824
|  | 2017-05-24 15:11 | 1003.9248 | 4.6786 | 9.737 | 30.4736 | 355.4005
|  | 2017-05-24 15:12 | 1003.8694 | 4.6735 | 9.7382 | 30.4903 | 355.4186
|  | 2017-05-24 15:13 | 1003.9329 | 4.6774 | 9.7394 | 30.5069 | 355.4367
|  | 2017-05-24 15:14 | 1003.9115 | 4.6991 | 9.7406 | 30.5236 | 355.4548
|  | 2017-05-24 15:15 | 1003.8491 | 4.7211 | 9.7418 | 30.5402 | 355.4729
|  | 2017-05-24 15:16 | 1003.8461 | 4.7432 | 9.743 | 30.5568 | 355.491
|  | 2017-05-24 15:17 | 1003.845 | 4.7653 | 9.7442 | 30.5735 | 355.5091
|  | 2017-05-24 15:18 | 1003.8444 | 4.7781 | 9.7454 | 30.5901 | 355.5272
|  | 2017-05-24 15:19 | 1003.8474 | 4.696 | 9.7466 | 30.6068 | 355.5453
|  | 2017-05-24 15:20 | 1003.8418 | 4.7177 | 9.7478 | 30.6234 | 355.5634
|  | 2017-05-24 15:21 | 1003.8472 | 4.7394 | 9.7489 | 30.6401 | 355.4735
|  | 2017-05-24 15:22 | 1003.8369 | 4.7611 | 9.7501 | 30.6567 | 355.2075
|  | 2017-05-24 15:23 | 1003.8376 | 4.7828 | 9.7513 | 30.6734 | 355.249
|  | 2017-05-24 15:24 | 1003.8428 | 4.8045 | 9.7525 | 30.69 | 355.5691
|  | 2017-05-24 15:25 | 1003.8417 | 4.7831 | 9.7537 | 30.6626 | 355.5006
|  | 2017-05-24 15:26 | 1003.8423 | 4.7644 | 9.7549 | 30.4549 | 355.121
|  | 2017-05-24 15:27 | 1003.847 | 4.7054 | 9.7561 | 30.2548 | 354.824
|  | 2017-05-24 15:28 | 1003.8455 | 4.7024 | 9.7572 | 30.225 | 355.3474
|  | 2017-05-24 15:29 | 1003.7996 | 4.6994 | 9.7575 | 30.225 | 355.3963
|  | 2017-05-24 15:30 | 1003.8428 | 4.6964 | 9.7575 | 30.225 | 355.1583
|  | 2017-05-24 15:31 | 1003.8447 | 4.6942 | 9.7575 | 30.225 | 355.1662
|  | 2017-05-24 15:32 | 1003.8455 | 4.694 | 9.7575 | 30.225 | 355.3666