## Machine1
To modify | Calculated |  |  | Flow [m3/h] | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110 | 115 | 120 | 125 | 130 | 135 | 140 | 145 | 150
∆P Piping [kPa]
Vol flow rate | 175 | m3/h
Actual DP | 91.77 | kPa |  |  | 15: Piping ∆P equation; 25: y=ax^b
[6 empty] | #NUM! |  |  | Coef a | #NUM! | Coef b | #NUM!
Various pressure drops
[13 empty] | EG30% | ρ [kg/m3] | µ [Pa-s]
[13 empty] | 15/10 | 1041.6 | 0.002734
Pipe section | Fluid | Specific gravity | Temperature | Dynamic viscosity | 10: Pipe internal diameter; 15: Pipe length; 20: Height difference DZ; 25: Roughness; 30: Relative roughness; 35: Mass flow rate; 40: Volumetric flow rate; 45: Fluid velocity; 50: Reynolds; 55: Moody friction factor; 70: Té soudé; 75: 0.3; 85: Bends; 105: Bends; 110: Alpha [°] | [5 empty] | Sum k | Valve and fitting pressure drop (Pa) | Straight pipe pressure drop | Elevation | Total
|  | rho | Temperature | mu | D | L | H | e | e/D | Qm | Qv | u | Re | A | B | f | Té normalisé | 1.5 |  | 90° elbow | -> | 1.5708 | rad | XX° Miter | 23 | 42 | 45 |  |  | x |  | Coupling |  |  | Ball Valve
|  | kg/m3 | c | Pa.s | m | m | m | mm | - | kg/h | m3/h | m/s | - |  |  |  | Number | k | Total k | Number | r | k | Total k | Number | 0.40143 | 0.73304 | 0.7854 |  |  | 0 | Total k | Number | k | Total k | Number | k | Total k | k | [5 empty] | kPa
Tronçon 1 | EG30% | 1041.6 | 15/10 | 0.002734 | 0.1071 | 2.388 | 0 | 0.045 | 0.00042017 | 182280 | 175 | 5.3959 | 220170.2607 | 1.3154e+21 | 5.0806e-13 | 0.018332 | 0 | 1.3 | 0 | 0 | 152 | 0.23567 | 0 | 0 | [6 empty] | 0 | 2 | 0.04 | 0.08 | 0 | 0.00099 | 0 |  | 0.08 | 0.012131 | 0.061981 | 0 | 0.074112 | 7.4112
Tronçon 2 | EG30% | 1041.6 | 15/10 | 0.002734 | 0.1071 | 0.612 | 0 | 0.045 | 0.00042017 | 182280 | 175 | 5.3959 | 220170.2607 | 1.3154e+21 | 5.0806e-13 | 0.018332 | 2 | 1.3 | 2.6 | 1 | 152 | 0.23567 | 0.23567 | 2 |  |  | 0.3042 |  |  |  | 0.60839 | 2 | 0.04 | 0.08 | 1 | 0.00099 | 0.00099 |  | 3.5251 | 0.53453 | 0.015885 | 0 | 0.55041 | 55.0413
Tronçon 3 | EG30% | 1041.6 | 15/10 | 0.002734 | 0.1071 | 2.9094 | 0 | 0.045 | 0.00042017 | 182280 | 175 | 5.3959 | 220170.2607 | 1.3154e+21 | 5.0806e-13 | 0.018332 | 0 | 1.3 | 0 | 3 | 152 | 0.23567 | 0.70702 | 2 |  |  | 0.3042 |  |  |  | 0.60839 | 3 | 0.04 | 0.12 | 0 | 0.00099 | 0 |  | 1.4354 | 0.21766 | 0.075514 | 0 | 0.29318 | 29.3176
[43 empty] | 0.9177 | bar | 91.77 | kPa
Note on V27: PARMENTIER, Thomas: Méthode Pipe Flow - Guide (2012)
Note on T28: PARMENTIER, Thomas: Méthode IDELCHIK https://www.hydraucalc.com/wp-content/uploads/delightful-downloads/2019/03/T%c3%a9-sym%c3%a9trique-brusque-avec-s%c3%a9paration-des-courants-soud%c3%a9-Section-circulaire-IDELCHIK-mar-2019.pdf
Note on X28: PARMENTIER, Thomas: Méthode Pipe Flow - Guide (2012) - Equation 15.1 https://www.hydraucalc.com/wp-content/uploads/delightful-downloads/2018/12/Coude-progressif-Section-circulaire-Pipe-Flow-Guide-nov-2018.pdf

## Machine 2
Valid in TURBULENT FLOW
Valid for incompressible fluid (~liquid)
Instruction
| 1 | Split the pipe layout in sections and describe sections line by line including the number of pipes and fitting in each section
| 2 | If you wish to calculate the pressure drop at a given mass flowrate, enter the flow in cell C13 and read the total pressure drop in cell C14. Pressure drop in each section is in column BP
| To modify | Calculated |  |  | Flow [m3/h] | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110 | 115 | 120 | 125 | 130 | 135 | 140 | 145 | 150
∆P Piping [kPa]
| Vol flow rate | 175 | m3/h
| Actual DP | 97.0978 | kPa |  |  | 15: Piping ∆P equation; 25: y=ax^b
[7 empty] | #NUM! |  |  | Coef a | #NUM! | Coef b | #NUM!
Various pressure drops
[14 empty] | EG30% | ρ [kg/m3] | µ [Pa-s]
[14 empty] | 15/10 | 1041.6 | 0.002734
| Pipe section | Fluid | Specific gravity | Temperature | Dynamic viscosity | 10: Pipe internal diameter; 15: Pipe length; 20: Height difference DZ; 25: Roughness; 30: Relative roughness; 35: Mass flow rate; 40: Volumetric flow rate; 45: Fluid velocity; 50: Reynolds; 55: Moody friction factor; 70: Té soudé; 75: 0.3; 85: Bends; 105: Bends; 110: Alpha [°] | [5 empty] | Sum k | Valve and fitting pressure drop (Pa) | Straight pipe pressure drop | Elevation | Total
|  |  | rho | Temperature | mu | D | L | H | e | e/D | Qm | Qv | u | Re | A | B | f | Té normalisé | 1.5 |  | 90° elbow | -> | 1.5708 | rad | XX° Miter | 23 | 42 | 45 |  |  | x |  | Coupling |  |  | Ball Valve
|  |  | kg/m3 | c | Pa.s | m | m | m | mm | - | kg/h | m3/h | m/s | - |  |  |  | Number | k | Total k | Number | r | k | Total k | Number | 0.40143 | 0.73304 | 0.7854 |  |  | 0 | Total k | Number | k | Total k | Number | k | Total k | k | [5 empty] | kPa
| Tronçon 1 | EG30% | 1041.6 | 15/10 | 0.002734 | 0.1071 | 2.388 | 0 | 0.045 | 0.00042017 | 182280 | 175 | 5.3959 | 220170.2607 | 1.3154e+21 | 5.0806e-13 | 0.018332 | 1 | 1.3 | 1.3 | 5 | 152 | 0.23567 | 1.1784 | 0 | [6 empty] | 0 | 1 | 0.04 | 0.04 | 0 | 0.00099 | 0 |  | 2.5184 | 0.38188 | 0.061981 | 0 | 0.44386 | 44.3859
| Tronçon 2 | EG30% | 1041.6 | 15/10 | 0.002734 | 0.1071 | 0.612 | 0 | 0.045 | 0.00042017 | 182280 | 175 | 5.3959 | 220170.2607 | 1.3154e+21 | 5.0806e-13 | 0.018332 | 0 | 1.3 | 0 | 1 | 152 | 0.23567 | 0.23567 | 2 |  |  | 0.3042 |  |  |  | 0.60839 | 2 | 0.04 | 0.08 | 1 | 0.00099 | 0.00099 |  | 0.92506 | 0.14027 | 0.015885 | 0 | 0.15616 | 15.6157
| Tronçon 3 | EG30% | 1041.6 | 15/10 | 0.002734 | 0.1071 | 2.9094 | 0 | 0.045 | 0.00042017 | 182280 | 175 | 5.3959 | 220170.2607 | 1.3154e+21 | 5.0806e-13 | 0.018332 | 1 | 1.3 | 1.3 | 0 | 152 | 0.23567 | 0 | 2 |  |  | 0.3042 |  |  |  | 0.60839 | 1 | 0.04 | 0.04 | 0 | 0.00099 | 0 |  | 1.9484 | 0.29545 | 0.075514 | 0 | 0.37096 | 37.0962
[44 empty] | 0.97098 | bar | 97.0978 | kPa
Note on V27: PARMENTIER, Thomas: Méthode Pipe Flow - Guide (2012)
Note on T28: PARMENTIER, Thomas: Méthode IDELCHIK https://www.hydraucalc.com/wp-content/uploads/delightful-downloads/2019/03/T%c3%a9-sym%c3%a9trique-brusque-avec-s%c3%a9paration-des-courants-soud%c3%a9-Section-circulaire-IDELCHIK-mar-2019.pdf
Note on X28: PARMENTIER, Thomas: Méthode Pipe Flow - Guide (2012) - Equation 15.1 https://www.hydraucalc.com/wp-content/uploads/delightful-downloads/2018/12/Coude-progressif-Section-circulaire-Pipe-Flow-Guide-nov-2018.pdf